## Job Info
Name | futu2
Scenario | ets_multi
Objective 1 | MIN_LIFE_CYCLE_COST
Objective 2 | MIN_FUEL_IMPORTS
Pareto points | 4
Temporal resolution | LOW
Optimality gap | 1
Time limit | 2880
Created at | 2025-02-21 01:07:08 (UTC)

## Key Results
Solution | Stage | Life-cycle cost (USD) | Annualized life-cycle cost (USD/year) | Capital recovery factor | CO2 emissions (kg-CO2) | Investment (USD) | Imports cost (USD) | Exports revenue (USD) | O&M cost (USD) | Replacement cost (USD) | Salvage revenue (USD) | Demands revenue (USD) | Embodied CO2 emissions (kg-CO2) | Imports CO2 emissions (kg-CO2) | Exports CO2 compensation (kg-CO2)
Solution 1 | stage0 | 117663984.4981 | 7155554.4667 | 0.060813 | 87120641.8932 | 58308134.994 | 51999145.1344 | 0 | 14443560.5489 | 0 | 7086856.1792 | 0 | 0 | 87120641.8932 | 0
Solution 2 | stage0 | 120071346.9639 | 7301954.517 | 0.060813 | 75300991.4644 | 69919210.7764 | 42487202.4632 | 20806.6428 | 16352985.6252 | 56.7303 | 8667301.9883 | 0 | 0 | 75300991.4644 | 0
Solution 3 | stage0 | 125493530.7011 | 7631696.2916 | 0.060813 | 59034001.3729 | 86425623.4989 | 30225339.1528 | 273675.364 | 18518996.9969 | 2581878.8801 | 11984632.4635 | 0 | 0 | 59034001.3729 | 0
Solution 4 | stage0 | 145069661.4444 | 8822188.6107 | 0.060813 | 41455984.4574 | 114640674.8457 | 18861212.5217 | 1062449.611 | 23638660.2922 | 4882773.3663 | 15891209.9705 | 0 | 0 | 41455984.4574 | 0

## Cost & CO2
Solution | Stage | Name | Type | Hub or Link | Capacity (kW or KWh) | Life-cycle cost (USD) | Annualized life-cycle cost (USD/year) | Investment (USD) | Imports cost (USD) | Exports revenue (USD) | O&M cost (USD) | Replacement cost (USD) | Salvage revenue (USD) | Embodied CO2 emissions (kg-CO2) | Imports CO2 emissions (kg-CO2) | Exports CO2 compensation (kg-CO2) | Lifetime (years) | Length (m) | Energy in (kWh/year) | Energy out (kWh/year)
Solution 1 | stage0 | Gas | Import | hub10 | 0 | -8.5265e-11 | -5.1853e-12 |  | -8.5265e-11 |  | 0 |  |  |  | -3.6115e-11 |  |  |  | -9.0288e-12
Solution 1 | stage0 | Gas | Import | hub8 | 0 | -7.8444e-09 | -4.7704e-10 |  | -7.8444e-09 |  | 0 |  |  |  | -6.7473e-11 |  |  |  | -1.6868e-11
Solution 1 | stage0 | Gas | Import | hub11 | 0.1 | 9.0949e-10 | 5.531e-11 |  | 9.0949e-10 |  | 0 |  |  |  | -2.5588e-10 |  |  |  | -6.3971e-11
Solution 1 | stage0 | Gas | Import | hub7 | 0 | 1.1369e-10 | 6.9137e-12 |  | 1.1369e-10 |  | 0 |  |  |  | -6.465e-11 |  |  |  | -1.6162e-11
Solution 1 | stage0 | Gas | Import | hub14 | 0.1 | -4.4793e-08 | -2.724e-09 |  | -4.4793e-08 |  | 0 |  |  |  | -1.9399e-07 |  |  |  | -4.8499e-08
Solution 1 | stage0 | Gas | Import | hub2 | 0.1 | 2.2737e-10 | 1.3827e-11 |  | 2.2737e-10 |  | 0 |  |  |  | -5.7981e-11 |  |  |  | -1.4495e-11
Solution 1 | stage0 | Gas | Import | hub3 | 0.1 | -2.2737e-10 | -1.3827e-11 |  | -2.2737e-10 |  | 0 |  |  |  | -3.3143e-11 |  |  |  | -8.2857e-12
Solution 1 | stage0 | Gas | Import | hub4 | 0.1 | -8.6402e-09 | -5.2544e-10 |  | -8.6402e-09 |  | 0 |  |  |  | -1.8075e-10 |  |  |  | -4.5187e-11
Solution 1 | stage0 | Gas | Import | hub6 | 0.1 | -4.2633e-11 | -2.5926e-12 |  | -4.2633e-11 |  | 0 |  |  |  | -4.1806e-11 |  |  |  | -1.0451e-11
Solution 1 | stage0 | Gas | Import | hub1 | 0.1 | -9.0949e-10 | -5.531e-11 |  | -9.0949e-10 |  | 0 |  |  |  | -5.5626e-10 |  |  |  | -1.3907e-10
Solution 1 | stage0 | Gas | Import | hub13 | 0 | 8.5265e-11 | 5.1853e-12 |  | 8.5265e-11 |  | 0 |  |  |  | -4.5387e-11 |  |  |  | -1.1347e-11
Solution 1 | stage0 | Gas | Import | hub5 | 0.1 | -4.7748e-09 | -2.9037e-10 |  | -4.7748e-09 |  | 0 |  |  |  | -7.9888e-11 |  |  |  | -1.9972e-11
Solution 1 | stage0 | Gas | Import | hub9 | 0.1 | 9.0949e-10 | 5.531e-11 |  | 9.0949e-10 |  | 0 |  |  |  | -4.334e-10 |  |  |  | -1.0835e-10
Solution 1 | stage0 | Gas | Import | hub12 | 0.1 | 2.9104e-08 | 1.7699e-09 |  | 2.9104e-08 |  | 0 |  |  |  | -5.1978e-09 |  |  |  | -1.2994e-09
Solution 1 | stage0 | Heat ambient in | Import | plant | 0 | 0 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0
Solution 1 | stage0 | Electricity | Import | hub10 | 34.8675 | 190889.803 | 11608.6701 |  | 190889.803 |  | 0 |  |  |  | 305602.7131 |  |  |  | 78608.4824
Solution 1 | stage0 | Electricity | Import | plant | 360.4152 | 2820840.0867 | 171545.0566 |  | 2820840.0867 |  | 0 |  |  |  | 5810313.1303 |  |  |  | 1412666.4401
Solution 1 | stage0 | Electricity | Import | hub8 | 194.6769 | 903827.0128 | 54964.8514 |  | 903827.0128 |  | 0 |  |  |  | 1552277.9701 |  |  |  | 354652.802
Solution 1 | stage0 | Electricity | Import | hub11 | 193.1701 | 1356015.9365 | 82464.0261 |  | 1356015.9365 |  | 0 |  |  |  | 2206691.6319 |  |  |  | 557713.6737
Solution 1 | stage0 | Electricity | Import | hub7 | 194.5424 | 886835.4698 | 53931.5368 |  | 886835.4698 |  | 0 |  |  |  | 1532331.9173 |  |  |  | 347928.8952
Solution 1 | stage0 | Electricity | Import | hub14 | 61.9532 | 330522.8928 | 20100.242 |  | 330522.8928 |  | 0 |  |  |  | 542660.2648 |  |  |  | 133278.6032
Solution 1 | stage0 | Electricity | Import | hub2 | 137.9834 | 780522.8921 | 47466.3007 |  | 780522.8921 |  | 0 |  |  |  | 1223945.8327 |  |  |  | 316929.226
Solution 1 | stage0 | Electricity | Import | hub3 | 90.1716 | 1077340.0289 | 65516.7789 |  | 1077340.0289 |  | 0 |  |  |  | 1740523.4485 |  |  |  | 439172.3066
Solution 1 | stage0 | Electricity | Import | hub4 | 497.7385 | 2412601.8106 | 146718.673 |  | 2412601.8106 |  | 0 |  |  |  | 4133889.1622 |  |  |  | 937727.3119
Solution 1 | stage0 | Electricity | Import | hub6 | 55.0449 | 92113.9931 | 5601.771 |  | 92113.9931 |  | 0 |  |  |  | 139763.0526 |  |  |  | 40681.9814
Solution 1 | stage0 | Electricity | Import | hub1 | 1569.8745 | 7670887.1673 | 466493.2194 |  | 7670887.1673 |  | 0 |  |  |  | 11220381.2492 |  |  |  | 3163423.6601
Solution 1 | stage0 | Electricity | Import | hub13 | 71.9467 | 243385.3167 | 14801.1042 |  | 243385.3167 |  | 0 |  |  |  | 407394.5141 |  |  |  | 105234.2544
Solution 1 | stage0 | Electricity | Import | hub5 | 281.6842 | 1376048.3423 | 83682.2661 |  | 1376048.3423 |  | 0 |  |  |  | 2364533.018 |  |  |  | 534771.5094
Solution 1 | stage0 | Electricity | Import | hub9 | 807.0325 | 6152749.8186 | 374170.0286 |  | 6152749.8186 |  | 0 |  |  |  | 10126335.379 |  |  |  | 2471877.2612
Solution 1 | stage0 | Electricity | Import | hub12 | 2168.0397 | 25704564.5631 | 1563183.6076 |  | 25704564.5631 |  | 0 |  |  |  | 43813998.6095 |  |  |  | 10689985.3595
Solution 1 | stage0 | Slack | Export | hub10 | 0.30656 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 83.9044
Solution 1 | stage0 | Slack | Export | hub8 | 0.58905 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 227.6923
Solution 1 | stage0 | Slack | Export | hub11 | 0.61341 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 503.1105
Solution 1 | stage0 | Slack | Export | hub7 | 0.58171 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 246.7497
Solution 1 | stage0 | Slack | Export | hub14 | 0.4369 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 216.1493
Solution 1 | stage0 | Slack | Export | hub2 | 1.1052 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 140.1151
Solution 1 | stage0 | Slack | Export | hub3 | 0.29564 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 79.1141
Solution 1 | stage0 | Slack | Export | hub4 | 1.4197 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 603.3812
Solution 1 | stage0 | Slack | Export | hub6 | 0.44146 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 106.3127
Solution 1 | stage0 | Slack | Export | hub1 | 8.8973 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 768.9111
Solution 1 | stage0 | Slack | Export | hub13 | 0.49702 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 122.6832
Solution 1 | stage0 | Slack | Export | hub5 | 0.79459 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 293.6841
Solution 1 | stage0 | Slack | Export | hub9 | 3.0105 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 965.4953
Solution 1 | stage0 | Slack | Export | hub12 | 3.8336 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 10889.1353
Solution 1 | stage0 | Heat ambient out | Export | plant | 1287.1972 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 7118778.9979
Solution 1 | stage0 | export_electricity | Export | plant | 0.1 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 0
Solution 1 | stage0 | parking to pv | Conversion | plant | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 25 |  | 0 | 0
Solution 1 | stage0 | cooling tower plant | Conversion | plant | 1287.1972 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 7118778.9979 | 7118778.9979
Solution 1 | stage0 | pv to hub | Conversion | hub1 | 37.6957 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 50503.9782 | 50503.9782
Solution 1 | stage0 | pv to hub | Conversion | hub10 | 0.66081 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 250.4488 | 250.4488
Solution 1 | stage0 | pv to hub | Conversion | hub11 | 2.9197 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 554.6758 | 554.6758
Solution 1 | stage0 | pv to hub | Conversion | hub12 | 5.003 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 963.0512 | 963.0512
Solution 1 | stage0 | pv to hub | Conversion | hub13 | 0.1 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 5.8 | 5.8
Solution 1 | stage0 | pv to hub | Conversion | hub14 | 3.3543 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 97.6379 | 97.6379
Solution 1 | stage0 | pv to hub | Conversion | hub2 | 18.0835 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 14503.8945 | 14503.8945
Solution 1 | stage0 | pv to hub | Conversion | hub3 | 3.0233 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 4477.5216 | 4477.5216
Solution 1 | stage0 | pv to hub | Conversion | hub4 | 9.2811 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 2452.6017 | 2452.6017
Solution 1 | stage0 | pv to hub | Conversion | hub5 | 1.5814 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 932.1929 | 932.1929
Solution 1 | stage0 | pv to hub | Conversion | hub6 | 18.2194 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 25854.1881 | 25854.1881
Solution 1 | stage0 | pv to hub | Conversion | hub7 | 0.1 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 16.4 | 16.4
Solution 1 | stage0 | pv to hub | Conversion | hub8 | 0.79303 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 58.7078 | 58.7078
Solution 1 | stage0 | pv to hub | Conversion | hub9 | 5.003 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 643.8117 | 643.8117
Solution 1 | stage0 | pv to electricity | Conversion | plant | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 0.0066144 | 0.0066144
Solution 1 | stage0 | Pump DHW gas | Conversion | hub1 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 1 | stage0 | Pump DHW gas | Conversion | hub10 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 1 | stage0 | Pump DHW gas | Conversion | hub11 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 1 | stage0 | Pump DHW gas | Conversion | hub12 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 1 | stage0 | Pump DHW gas | Conversion | hub13 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 1 | stage0 | Pump DHW gas | Conversion | hub14 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 1 | stage0 | Pump DHW gas | Conversion | hub2 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 1 | stage0 | Pump DHW gas | Conversion | hub3 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 1 | stage0 | Pump DHW gas | Conversion | hub4 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 1 | stage0 | Pump DHW gas | Conversion | hub5 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 1 | stage0 | Pump DHW gas | Conversion | hub6 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 1 | stage0 | Pump DHW gas | Conversion | hub7 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 1 | stage0 | Pump DHW gas | Conversion | hub8 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 1 | stage0 | Pump DHW gas | Conversion | hub9 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 1 | stage0 | HEX pump ETS | Conversion | hub1 | 1506.007 | 1009648.2876 | 61400.2096 | 759776.9816 |  |  | 249871.306 | 0 | 0 | 0 |  |  | 20 |  | 381512.9215 | 381512.9215
Solution 1 | stage0 | HEX pump ETS | Conversion | hub10 | 106.6678 | 479677.6208 | 29170.8577 | 360965.3177 |  |  | 118712.3031 | 0 | 0 | 0 |  |  | 20 |  | 41905.6002 | 41905.6002
Solution 1 | stage0 | HEX pump ETS | Conversion | hub11 | 167.2098 | 502606.647 | 30565.2512 | 378219.7879 |  |  | 124386.8591 | 0 | 0 | 0 |  |  | 20 |  | 247090.4591 | 247090.4591
Solution 1 | stage0 | HEX pump ETS | Conversion | hub12 | 1916.7844 | 1165221.729 | 70861.1695 | 876848.5611 |  |  | 288373.1679 | 0 | 0 | 0 |  |  | 20 |  | 5444567.6537 | 5444567.6537
Solution 1 | stage0 | HEX pump ETS | Conversion | hub13 | 103.75 | 478572.553 | 29103.6546 | 360133.736 |  |  | 118438.8171 | 0 | 0 | 0 |  |  | 20 |  | 58147.5957 | 58147.5957
Solution 1 | stage0 | HEX pump ETS | Conversion | hub14 | 107.4477 | 479972.9898 | 29188.8201 | 361187.5877 |  |  | 118785.4021 | 0 | 0 | 0 |  |  | 20 |  | 107963.6251 | 107963.6251
Solution 1 | stage0 | HEX pump ETS | Conversion | hub2 | 202.6796 | 516040.1028 | 31382.1861 | 388328.6849 |  |  | 127711.418 | 0 | 0 | 0 |  |  | 20 |  | 68563.5179 | 68563.5179
Solution 1 | stage0 | HEX pump ETS | Conversion | hub3 | 40.274 | 454532.3358 | 27641.6858 | 342043.0762 |  |  | 112489.2596 | 0 | 0 | 0 |  |  | 20 |  | 35618.2025 | 35618.2025
Solution 1 | stage0 | HEX pump ETS | Conversion | hub4 | 185.8581 | 509669.3276 | 30994.7572 | 383534.5715 |  |  | 126134.7561 | 0 | 0 | 0 |  |  | 20 |  | 279910.2334 | 279910.2334
Solution 1 | stage0 | HEX pump ETS | Conversion | hub5 | 89.2241 | 473071.1732 | 28769.0967 | 355993.8569 |  |  | 117077.3162 | 0 | 0 | 0 |  |  | 20 |  | 134681.4444 | 134681.4444
Solution 1 | stage0 | HEX pump ETS | Conversion | hub6 | 83.8601 | 471039.6701 | 28645.5539 | 354465.1173 |  |  | 116574.5527 | 0 | 0 | 0 |  |  | 20 |  | 52608.8566 | 52608.8566
Solution 1 | stage0 | HEX pump ETS | Conversion | hub7 | 68.8388 | 465350.696 | 28299.5877 | 350184.0706 |  |  | 115166.6254 | 0 | 0 | 0 |  |  | 20 |  | 114191.9287 | 114191.9287
Solution 1 | stage0 | HEX pump ETS | Conversion | hub8 | 65.8765 | 464228.7631 | 28231.3591 | 349339.7976 |  |  | 114888.9655 | 0 | 0 | 0 |  |  | 20 |  | 103531.2546 | 103531.2546
Solution 1 | stage0 | HEX pump ETS | Conversion | hub9 | 463.8445 | 614950.8707 | 37397.2925 | 462760.6684 |  |  | 152190.2024 | 0 | 0 | 0 |  |  | 20 |  | 478355.0326 | 478355.0326
Solution 1 | stage0 | Main HP | Conversion | plant | 1158.4775 | 2510877.5285 | 152695.1598 | 1889476.7348 |  |  | 621400.7937 | 0 | 0 | 0 |  |  | 20 |  | 6406901.0981 | 6406901.0981
Solution 1 | stage0 | Pump cooling | Conversion | hub1 | 2746.524 | 171158.67 | 10408.7516 | 128799.7209 |  |  | 42358.9491 | 0 | 0 | 0 |  |  | 20 |  | 2915759.2445 | 2915759.2445
Solution 1 | stage0 | Pump cooling | Conversion | hub10 | 43.5653 | 63401.8789 | 3855.6879 | 47710.9591 |  |  | 15690.9198 | 0 | 0 | 0 |  |  | 20 |  | 40007.4138 | 40007.4138
Solution 1 | stage0 | Pump cooling | Conversion | hub11 | 266.7618 | 72299.8815 | 4396.8062 | 54406.8527 |  |  | 17893.0287 | 0 | 0 | 0 |  |  | 20 |  | 591625.2592 | 591625.2592
Solution 1 | stage0 | Pump cooling | Conversion | hub12 | 4679.9342 | 248236.4561 | 15096.1187 | 186802.0256 |  |  | 61434.4304 | 0 | 0 | 0 |  |  | 20 |  | 9316324.8382 | 9316324.8382
Solution 1 | stage0 | Pump cooling | Conversion | hub13 | 151.9881 | 67724.2879 | 4118.5485 | 50963.6432 |  |  | 16760.6448 | 0 | 0 | 0 |  |  | 20 |  | 69307.0831 | 69307.0831
Solution 1 | stage0 | Pump cooling | Conversion | hub14 | 103.6616 | 65797.6909 | 4001.3855 | 49513.8471 |  |  | 16283.8437 | 0 | 0 | 0 |  |  | 20 |  | 51168.1813 | 51168.1813
Solution 1 | stage0 | Pump cooling | Conversion | hub2 | 326.6423 | 74687.0943 | 4541.9809 | 56203.2698 |  |  | 18483.8245 | 0 | 0 | 0 |  |  | 20 |  | 228166.8433 | 228166.8433
Solution 1 | stage0 | Pump cooling | Conversion | hub3 | 100.4378 | 65669.1709 | 3993.5697 | 49417.1337 |  |  | 16252.0372 | 0 | 0 | 0 |  |  | 20 |  | 131510.3058 | 131510.3058
Solution 1 | stage0 | Pump cooling | Conversion | hub4 | 748.031 | 91486.2748 | 5563.5973 | 68844.9301 |  |  | 22641.3448 | 0 | 0 | 0 |  |  | 20 |  | 811707.9698 | 811707.9698
Solution 1 | stage0 | Pump cooling | Conversion | hub5 | 380.9923 | 76853.8252 | 4673.7473 | 57833.7705 |  |  | 19020.0547 | 0 | 0 | 0 |  |  | 20 |  | 422265.8725 | 422265.8725
Solution 1 | stage0 | Pump cooling | Conversion | hub6 | 127.8045 | 66760.1774 | 4059.9176 | 50238.1341 |  |  | 16522.0433 | 0 | 0 | 0 |  |  | 20 |  | 33799.1385 | 33799.1385
Solution 1 | stage0 | Pump cooling | Conversion | hub7 | 264.3832 | 72205.0571 | 4391.0396 | 54335.4958 |  |  | 17869.5612 | 0 | 0 | 0 |  |  | 20 |  | 292396.6081 | 292396.6081
Solution 1 | stage0 | Pump cooling | Conversion | hub8 | 267.1967 | 72317.22 | 4397.8606 | 54419.9003 |  |  | 17897.3197 | 0 | 0 | 0 |  |  | 20 |  | 309788.5739 | 309788.5739
Solution 1 | stage0 | Pump cooling | Conversion | hub9 | 1086.2268 | 104968.8674 | 6383.5204 | 78990.8032 |  |  | 25978.0642 | 0 | 0 | 0 |  |  | 20 |  | 1693852.2016 | 1693852.2016
Solution 1 | stage0 | Pump DHW | Conversion | hub1 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 1 | stage0 | Pump DHW | Conversion | hub10 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 1 | stage0 | Pump DHW | Conversion | hub11 | 34.8297 | 8790.9289 | 534.6068 | 6615.3189 |  |  | 2175.61 | 0 | 0 | 0 |  |  | 20 |  | 157809.6407 | 157809.6407
Solution 1 | stage0 | Pump DHW | Conversion | hub12 | 554.1475 | 11551.3616 | 702.4783 | 8692.59 |  |  | 2858.7716 | 0 | 0 | 0 |  |  | 20 |  | 3432869.3219 | 3432869.3219
Solution 1 | stage0 | Pump DHW | Conversion | hub13 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 1 | stage0 | Pump DHW | Conversion | hub14 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 1 | stage0 | Pump DHW | Conversion | hub2 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 1 | stage0 | Pump DHW | Conversion | hub3 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 1 | stage0 | Pump DHW | Conversion | hub4 | 94.6748 | 9109.0353 | 553.952 | 6854.6992 |  |  | 2254.3361 | 0 | 0 | 0 |  |  | 20 |  | 355179.8886 | 355179.8886
Solution 1 | stage0 | Pump DHW | Conversion | hub5 | 55.1879 | 8899.1428 | 541.1877 | 6696.7517 |  |  | 2202.3911 | 0 | 0 | 0 |  |  | 20 |  | 207042.1928 | 207042.1928
Solution 1 | stage0 | Pump DHW | Conversion | hub6 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 1 | stage0 | Pump DHW | Conversion | hub7 | 43.6957 | 8838.056 | 537.4728 | 6650.7829 |  |  | 2187.2732 | 0 | 0 | 0 |  |  | 20 |  | 163928.5463 | 163928.5463
Solution 1 | stage0 | Pump DHW | Conversion | hub8 | 43.6957 | 8838.056 | 537.4728 | 6650.7829 |  |  | 2187.2732 | 0 | 0 | 0 |  |  | 20 |  | 163928.5463 | 163928.5463
Solution 1 | stage0 | Pump DHW | Conversion | hub9 | 71.4402 | 8985.5316 | 546.4413 | 6761.7607 |  |  | 2223.7709 | 0 | 0 | 0 |  |  | 20 |  | 268013.7936 | 268013.7936
Solution 1 | stage0 | Pump SH | Conversion | hub1 | 2304.5377 | 203386.154 | 12368.6165 | 153051.434 |  |  | 50334.7201 | 0 | 0 | 0 |  |  | 20 |  | 769002.1132 | 769002.1132
Solution 1 | stage0 | Pump SH | Conversion | hub10 | 135.9123 | 93876.5701 | 5708.9594 | 70643.6666 |  |  | 23232.9034 | 0 | 0 | 0 |  |  | 20 |  | 51886.8029 | 51886.8029
Solution 1 | stage0 | Pump SH | Conversion | hub11 | 218.5355 | 98048.8117 | 5962.6879 | 73783.3473 |  |  | 24265.4645 | 0 | 0 | 0 |  |  | 20 |  | 358030.5729 | 358030.5729
Solution 1 | stage0 | Pump SH | Conversion | hub12 | 2153.8699 | 195777.846 | 11905.929 | 147326.0568 |  |  | 48451.7893 | 0 | 0 | 0 |  |  | 20 |  | 7345736.8521 | 7345736.8521
Solution 1 | stage0 | Pump SH | Conversion | hub13 | 140.401 | 94103.2358 | 5722.7437 | 70814.2363 |  |  | 23288.9995 | 0 | 0 | 0 |  |  | 20 |  | 72255.5737 | 72255.5737
Solution 1 | stage0 | Pump SH | Conversion | hub14 | 142.1925 | 94193.7038 | 5728.2454 | 70882.315 |  |  | 23311.3888 | 0 | 0 | 0 |  |  | 20 |  | 133678.2323 | 133678.2323
Solution 1 | stage0 | Pump SH | Conversion | hub2 | 279.8181 | 101143.4144 | 6150.8814 | 76112.0868 |  |  | 25031.3276 | 0 | 0 | 0 |  |  | 20 |  | 85065.6119 | 85065.6119
Solution 1 | stage0 | Pump SH | Conversion | hub3 | 58.7399 | 89979.5802 | 5471.9699 | 67711.1175 |  |  | 22268.4627 | 0 | 0 | 0 |  |  | 20 |  | 44423.8362 | 44423.8362
Solution 1 | stage0 | Pump SH | Conversion | hub4 | 273.5294 | 100825.8515 | 6131.5693 | 75873.1155 |  |  | 24952.736 | 0 | 0 | 0 |  |  | 20 |  | 263452.5885 | 263452.5885
Solution 1 | stage0 | Pump SH | Conversion | hub5 | 136.167 | 93889.4307 | 5709.7415 | 70653.3444 |  |  | 23236.0862 | 0 | 0 | 0 |  |  | 20 |  | 116315.6148 | 116315.6148
Solution 1 | stage0 | Pump SH | Conversion | hub6 | 115.1239 | 92826.813 | 5645.12 | 69853.7071 |  |  | 22973.1059 | 0 | 0 | 0 |  |  | 20 |  | 65178.3221 | 65178.3221
Solution 1 | stage0 | Pump SH | Conversion | hub7 | 104.0534 | 92267.7852 | 5611.1236 | 69433.0295 |  |  | 22834.7557 | 0 | 0 | 0 |  |  | 20 |  | 100816.5425 | 100816.5425
Solution 1 | stage0 | Pump SH | Conversion | hub8 | 100.9653 | 92111.8452 | 5601.6404 | 69315.682 |  |  | 22796.1631 | 0 | 0 | 0 |  |  | 20 |  | 97713.9952 | 97713.9952
Solution 1 | stage0 | Pump SH | Conversion | hub9 | 674.3585 | 121066.6146 | 7362.4802 | 91104.6234 |  |  | 29961.9912 | 0 | 0 | 0 |  |  | 20 |  | 577006.576 | 577006.576
Solution 1 | stage0 | HEX SC ets | Conversion | hub1 | 8.8973 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 768911.123 | 768.9111
Solution 1 | stage0 | HEX SC ets | Conversion | hub10 | 0.30656 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 83904.426 | 83.9044
Solution 1 | stage0 | HEX SC ets | Conversion | hub11 | 0.61341 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 503110.5292 | 503.1105
Solution 1 | stage0 | HEX SC ets | Conversion | hub12 | 3.8336 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 10889135.3074 | 10889.1353
Solution 1 | stage0 | HEX SC ets | Conversion | hub13 | 0.49702 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 122683.2402 | 122.6832
Solution 1 | stage0 | HEX SC ets | Conversion | hub14 | 0.4369 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 216149.2536 | 216.1493
Solution 1 | stage0 | HEX SC ets | Conversion | hub2 | 1.1052 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 140115.1011 | 140.1151
Solution 1 | stage0 | HEX SC ets | Conversion | hub3 | 0.29564 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 79114.0515 | 79.1141
Solution 1 | stage0 | HEX SC ets | Conversion | hub4 | 1.4197 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 603381.1777 | 603.3812
Solution 1 | stage0 | HEX SC ets | Conversion | hub5 | 0.79459 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 293684.0729 | 293.6841
Solution 1 | stage0 | HEX SC ets | Conversion | hub6 | 0.44146 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 106312.6657 | 106.3127
Solution 1 | stage0 | HEX SC ets | Conversion | hub7 | 0.58171 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 246749.7364 | 246.7497
Solution 1 | stage0 | HEX SC ets | Conversion | hub8 | 0.58905 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 227692.3005 | 227.6923
Solution 1 | stage0 | HEX SC ets | Conversion | hub9 | 3.0105 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 965495.3393 | 965.4953
Solution 1 | stage0 | ETS HP | Conversion | hub1 | 2942.74 | 8160047.4971 | 496240.7534 | 6140570.2691 |  |  | 2019477.228 | 0 | 0 | 0 |  |  | 20 |  | 191367.7909 | 2870470.1745
Solution 1 | stage0 | ETS HP | Conversion | hub10 | 46.7128 | 155257.2966 | 9441.734 | 116833.6753 |  |  | 38423.6213 | 0 | 0 | 0 |  |  | 20 |  | 2863.761 | 42918.5979
Solution 1 | stage0 | ETS HP | Conversion | hub11 | 308.2411 | 878136.8706 | 53402.5448 | 660812.4722 |  |  | 217324.3984 | 0 | 0 | 0 |  |  | 20 |  | 66638.3851 | 655089.0426
Solution 1 | stage0 | ETS HP | Conversion | hub12 | 5306.7548 | 14694323.8784 | 893612.7339 | 11057720.9709 |  |  | 3636602.9075 | 0 | 0 | 0 |  |  | 20 |  | 1206429.8712 | 10767156.3819
Solution 1 | stage0 | ETS HP | Conversion | hub13 | 162.8801 | 476350.5423 | 28968.5265 | 358461.6362 |  |  | 117888.906 | 0 | 0 | 0 |  |  | 20 |  | 5166.8776 | 77459.6602
Solution 1 | stage0 | ETS HP | Conversion | hub14 | 111.1017 | 333231.9035 | 20264.9863 | 250762.5011 |  |  | 82469.4024 | 0 | 0 | 0 |  |  | 20 |  | 3663.868 | 54937.8166
Solution 1 | stage0 | ETS HP | Conversion | hub2 | 350.0096 | 993587.5886 | 60423.5029 | 747691.0408 |  |  | 245896.5478 | 0 | 0 | 0 |  |  | 20 |  | 16396.7031 | 245917.5557
Solution 1 | stage0 | ETS HP | Conversion | hub3 | 107.6476 | 323684.7024 | 19684.3879 | 243578.0749 |  |  | 80106.6275 | 0 | 0 | 0 |  |  | 20 |  | 9665.429 | 144863.7393
Solution 1 | stage0 | ETS HP | Conversion | hub4 | 904.2163 | 2525447.4657 | 153581.2081 | 1900440.8527 |  |  | 625006.6129 | 0 | 0 | 0 |  |  | 20 |  | 127056.446 | 1107500.9496
Solution 1 | stage0 | ETS HP | Conversion | hub5 | 454.5568 | 1282562.0911 | 77997.0433 | 965149.118 |  |  | 317412.9731 | 0 | 0 | 0 |  |  | 20 |  | 70231.9829 | 591582.3989
Solution 1 | stage0 | ETS HP | Conversion | hub6 | 136.9691 | 404730.9017 | 24613.0881 | 304566.676 |  |  | 100164.2257 | 0 | 0 | 0 |  |  | 20 |  | 2453.6662 | 36768.7341
Solution 1 | stage0 | ETS HP | Conversion | hub7 | 317.2977 | 903169.7426 | 54924.8805 | 679650.121 |  |  | 223519.6215 | 0 | 0 | 0 |  |  | 20 |  | 52862.1144 | 424089.1059
Solution 1 | stage0 | ETS HP | Conversion | hub8 | 318.2995 | 905938.7662 | 55093.2744 | 681733.857 |  |  | 224204.9092 | 0 | 0 | 0 |  |  | 20 |  | 53751.083 | 435535.9904
Solution 1 | stage0 | ETS HP | Conversion | hub9 | 1231.827 | 3430982.795 | 208649.9481 | 2581871.1168 |  |  | 849111.6782 | 0 | 0 | 0 |  |  | 20 |  | 173500.4253 | 1949370.1469
Solution 1 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub1 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -2.2397e-11 | -2.0157e-11
Solution 1 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub10 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -1.7615e-12 | -1.5854e-12
Solution 1 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub11 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -1.3512e-11 | -1.216e-11
Solution 1 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub12 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -2.8422e-10 | -2.558e-10
Solution 1 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub13 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -1.7238e-12 | -1.5514e-12
Solution 1 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub14 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -4.8481e-08 | -4.3633e-08
Solution 1 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub2 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -3.0027e-12 | -2.7024e-12
Solution 1 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub3 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -2.3916e-12 | -2.1524e-12
Solution 1 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub4 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -7.8289e-12 | -7.046e-12
Solution 1 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub5 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -4.184e-12 | -3.7656e-12
Solution 1 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub6 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -1.9171e-12 | -1.7254e-12
Solution 1 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub7 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -3.4385e-12 | -3.0947e-12
Solution 1 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub8 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -3.0405e-12 | -2.7364e-12
Solution 1 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub9 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -2.3405e-11 | -2.1065e-11
Solution 1 | stage0 | rooftop to pv | Conversion | plant | 76.734 | 276168.3743 | 16794.7554 | 268568.8417 |  |  | 44162.7273 | 0 | 36563.1947 | 0 |  |  | 25 |  | 101314.917 | 101314.917
Solution 1 | stage0 | battery | Storage | plant | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 15 |  | 0 | 0
Solution 1 | stage0 | Generic Hot Water Storage hub1 | Storage | hub1 | 0.27367 | 14949.1296 | 909.1084 | 13813.4099 |  |  | 1135.7197 | 0 | 0 | 0 |  |  | 20 |  | 23.3449 | 0
Solution 1 | stage0 | Generic Hot Water Storage hub2 | Storage | hub2 | 0.19151 | 14944.7727 | 908.8434 | 13809.384 |  |  | 1135.3887 | 0 | 0 | 0 |  |  | 20 |  | 16.4957 | 0
Solution 1 | stage0 | Generic Hot Water Storage hub3 | Storage | hub3 | 0.6601 | 14969.6216 | 910.3545 | 13832.3451 |  |  | 1137.2765 | 0 | 0 | 0 |  |  | 20 |  | 58.8476 | 0
Solution 1 | stage0 | Generic Hot Water Storage hub4 | Storage | hub4 | 494.4199 | 41153.0668 | 2502.6605 | 38026.5738 |  |  | 3126.493 | 0 | 0 | 0 |  |  | 20 |  | 174392.7481 | 130399.7664
Solution 1 | stage0 | Generic Hot Water Storage hub5 | Storage | hub5 | 270.1843 | 29262.1449 | 1779.5324 | 27039.0325 |  |  | 2223.1124 | 0 | 0 | 0 |  |  | 20 |  | 96914.9072 | 73008.4277
Solution 1 | stage0 | Generic Hot Water Storage hub6 | Storage | hub6 | 0.26712 | 14948.7824 | 909.0872 | 13813.0891 |  |  | 1135.6933 | 0 | 0 | 0 |  |  | 20 |  | 18.1295 | 8.8339e-10
Solution 1 | stage0 | Generic Hot Water Storage hub7 | Storage | hub7 | 245.2537 | 27940.1061 | 1699.1346 | 25817.4321 |  |  | 2122.674 | 0 | 0 | 0 |  |  | 20 |  | 80753.9614 | 60261.2024
Solution 1 | stage0 | Generic Hot Water Storage hub8 | Storage | hub8 | 250.1121 | 28197.7397 | 1714.8022 | 26055.4927 |  |  | 2142.247 | 0 | 0 | 0 |  |  | 20 |  | 83156.9817 | 61720.4007
Solution 1 | stage0 | Generic Hot Water Storage hub9 | Storage | hub9 | 640.8508 | 48918.1104 | 2974.8797 | 45201.6892 |  |  | 3716.4212 | 0 | 0 | 0 |  |  | 20 |  | 170847.2933 | 112292.9706
Solution 1 | stage0 | Generic Hot Water Storage hub10 | Storage | hub10 | 0.29546 | 14950.2853 | 909.1786 | 13814.4778 |  |  | 1135.8075 | 0 | 0 | 0 |  |  | 20 |  | 18.9083 | 0
Solution 1 | stage0 | Generic Hot Water Storage hub11 | Storage | hub11 | 180.8518 | 24524.9533 | 1491.4474 | 22661.7363 |  |  | 1863.217 | 0 | 0 | 0 |  |  | 20 |  | 62152.2713 | 47718.5448
Solution 1 | stage0 | Generic Hot Water Storage hub12 | Storage | hub12 | 3112.2186 | 179971.5641 | 10944.6942 | 166298.7111 |  |  | 13672.8531 | 0 | 0 | 0 |  |  | 20 |  | 1149918.7859 | 918142.2649
Solution 1 | stage0 | Generic Hot Water Storage hub13 | Storage | hub13 | 0.26628 | 14948.7376 | 909.0845 | 13813.0477 |  |  | 1135.6899 | 0 | 0 | 0 |  |  | 20 |  | 21.7523 | 0
Solution 1 | stage0 | Generic Hot Water Storage hub14 | Storage | hub14 | 0.16049 | 14943.1279 | 908.7434 | 13807.8641 |  |  | 1135.2637 | 0 | 0 | 0 |  |  | 20 |  | 10.102 | 5.5618e-10
Solution 1 | stage0 | Generic Borehole | Storage | plant | 9500000 | 10571597.206 | 642895.4444 | 14250000 |  |  | 1171615.5519 | 0 | 4850018.3459 | 0 |  |  | 40 |  | 11178645.5383 | 9715914.2315
Solution 1 | stage0 | Anergy | Network | hub1_to_hub2_Anergy | 7735.8223 | 478628.6295 | 29107.0649 | 580800 |  |  | 95505.1667 | 0 | 197676.5372 | 0 |  |  | 40 | 528 | 6923056.3351 | 11522845.3534
Solution 1 | stage0 | Anergy | Network | hub3_to_hub4_Anergy | 7405.6881 | 452340.3146 | 27508.3814 | 548900 |  |  | 90259.6177 | 0 | 186819.3032 | 0 |  |  | 40 | 499 | 6831310.9327 | 11137525.2353
Solution 1 | stage0 | Anergy | Network | hub5_to_hub6_Anergy | 6515.1791 | 317272.7657 | 19294.4559 | 385000 |  |  | 63308.3491 | 0 | 131035.5834 | 0 |  |  | 40 | 350 | 6434302.9158 | 10083184.2495
Solution 1 | stage0 | Anergy | Network | hub7_to_hub8_Anergy | 6244.3897 | 180392.2297 | 10970.2763 | 218900 |  |  | 35995.3185 | 0 | 74503.0888 | 0 |  |  | 40 | 199 | 6273331.3755 | 9811317.3318
Solution 1 | stage0 | Anergy | Network | hub9_to_hub10_Anergy | 5034.4096 | 758735.1569 | 46141.313 | 920700 |  |  | 151397.3949 | 0 | 313362.238 | 0 |  |  | 40 | 837 | 5741383.1737 | 7940795.0693
Solution 1 | stage0 | Anergy | Network | hub11_to_hub12_Anergy | 4749.8369 | 591940.3315 | 35997.9419 | 718300 |  |  | 118115.2914 | 0 | 244474.9598 | 0 |  |  | 40 | 653 | 5469957.8938 | 7416542.0275
Solution 1 | stage0 | Anergy | Network | hub13_to_hub14_Anergy | 113.8479 | 383446.7997 | 23318.7281 | 465300 |  |  | 76512.6619 | 0 | 158365.8622 | 0 |  |  | 40 | 423 | 105264.5345 | 56222.2696
Solution 1 | stage0 | pv_loop | Network | hub1_to_hub2_pv_loop | 39.0382 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 528 | 50810.9322 | 0
Solution 1 | stage0 | pv_loop | Network | hub3_to_hub4_pv_loop | 18.7548 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 499 | 31829.516 | 0
Solution 1 | stage0 | pv_loop | Network | hub5_to_hub6_pv_loop | 18.7548 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 350 | 28444.7214 | 0
Solution 1 | stage0 | pv_loop | Network | hub7_to_hub8_pv_loop | 5.003 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 199 | 2574.1332 | 0
Solution 1 | stage0 | pv_loop | Network | hub9_to_hub10_pv_loop | 5.003 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 837 | 1871.6137 | 0
Solution 1 | stage0 | pv_loop | Network | hub11_to_hub12_pv_loop | 5.003 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 653 | 1066.4892 | 0
Solution 1 | stage0 | pv_loop | Network | hub13_to_hub14_pv_loop | 3.3543 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 423 | 97.6379 | 0
Solution 1 | stage0 | Anergy | Network | plant_to_hub1_Anergy | 10491.3558 | 94275.3361 | 5733.2097 | 114400 |  |  | 18811.6237 | 0 | 38936.2876 | 0 |  |  | 40 | 104 | 7094385.9612 | 14263229.8192
Solution 1 | stage0 | Anergy | Network | hub2_to_hub3_Anergy | 7515.2728 | 109685.7276 | 6670.369 | 133100 |  |  | 21886.6007 | 0 | 45300.8731 | 0 |  |  | 40 | 121 | 6865636.2965 | 11281600.8705
Solution 1 | stage0 | Anergy | Network | hub4_to_hub5_Anergy | 6773.3766 | 119657.1574 | 7276.7662 | 145200 |  |  | 23876.2917 | 0 | 49419.1343 | 0 |  |  | 40 | 132 | 6563499.9909 | 10438475.2594
Solution 1 | stage0 | Anergy | Network | hub6_to_hub7_Anergy | 6440.2743 | 145945.4722 | 8875.4497 | 177100 |  |  | 29121.8406 | 0 | 60276.3684 | 0 |  |  | 40 | 161 | 6383351.9706 | 10046395.5258
Solution 1 | stage0 | Anergy | Network | hub8_to_hub9_Anergy | 6102.4018 | 1264558.5949 | 76902.1884 | 1534500 |  |  | 252328.9915 | 0 | 522270.3966 | 0 |  |  | 40 | 1395 | 6174251.3897 | 9567174.1989
Solution 1 | stage0 | Anergy | Network | hub10_to_hub11_Anergy | 4987.7493 | 144132.485 | 8765.1957 | 174900 |  |  | 28760.0786 | 0 | 59527.5936 | 0 |  |  | 40 | 159 | 5700569.7224 | 7896887.7046
Solution 1 | stage0 | Anergy | Network | hub12_to_hub13_Anergy | 228.6848 | 286451.9828 | 17420.1373 | 347600 |  |  | 57158.3952 | 0 | 118306.4124 | 0 |  |  | 40 | 316 | 161957.8688 | 132369.271
Solution 1 | stage0 | pv_loop | Network | plant_to_hub1_pv_loop | 76.734 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 104 | 101314.9104 | 0
Solution 1 | stage0 | pv_loop | Network | hub2_to_hub3_pv_loop | 20.9548 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 121 | 36307.0377 | 0
Solution 1 | stage0 | pv_loop | Network | hub4_to_hub5_pv_loop | 18.7548 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 132 | 29376.9143 | 0
Solution 1 | stage0 | pv_loop | Network | hub6_to_hub7_pv_loop | 5.003 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 161 | 2590.5332 | 0
Solution 1 | stage0 | pv_loop | Network | hub8_to_hub9_pv_loop | 5.003 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 1395 | 2515.4255 | 0
Solution 1 | stage0 | pv_loop | Network | hub10_to_hub11_pv_loop | 5.003 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 159 | 1621.165 | 0
Solution 1 | stage0 | pv_loop | Network | hub12_to_hub13_pv_loop | 3.3543 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 316 | 103.4379 | 0
Solution 2 | stage0 | Gas | Import | hub10 | 0 | -8.3142e-12 | -5.0561e-13 |  | -8.3142e-12 |  | 0 |  |  |  | -3.6115e-11 |  |  |  | -9.0288e-12
Solution 2 | stage0 | Gas | Import | hub8 | 0 | -1.5584e-11 | -9.4773e-13 |  | -1.5584e-11 |  | 0 |  |  |  | -6.7695e-11 |  |  |  | -1.6924e-11
Solution 2 | stage0 | Gas | Import | hub11 | 0 | -5.8907e-11 | -3.5824e-12 |  | -5.8907e-11 |  | 0 |  |  |  | -2.5588e-10 |  |  |  | -6.3971e-11
Solution 2 | stage0 | Gas | Import | hub7 | 0 | -1.4883e-11 | -9.051e-13 |  | -1.4883e-11 |  | 0 |  |  |  | -6.465e-11 |  |  |  | -1.6162e-11
Solution 2 | stage0 | Gas | Import | hub14 | 0 | -2.1809e-11 | -1.3263e-12 |  | -2.1809e-11 |  | 0 |  |  |  | -9.4736e-11 |  |  |  | -2.3684e-11
Solution 2 | stage0 | Gas | Import | hub2 | 0 | -1.3348e-11 | -8.1174e-13 |  | -1.3348e-11 |  | 0 |  |  |  | -5.7981e-11 |  |  |  | -1.4495e-11
Solution 2 | stage0 | Gas | Import | hub3 | 0 | -7.7359e-12 | -4.7045e-13 |  | -7.7359e-12 |  | 0 |  |  |  | -3.3603e-11 |  |  |  | -8.4008e-12
Solution 2 | stage0 | Gas | Import | hub4 | 0 | -4.2019e-11 | -2.5553e-12 |  | -4.2019e-11 |  | 0 |  |  |  | -1.8252e-10 |  |  |  | -4.5631e-11
Solution 2 | stage0 | Gas | Import | hub6 | 0 | -1.0059e-11 | -6.117e-13 |  | -1.0059e-11 |  | 0 |  |  |  | -4.3693e-11 |  |  |  | -1.0923e-11
Solution 2 | stage0 | Gas | Import | hub1 | 0 | -1.2806e-10 | -7.7877e-12 |  | -1.2806e-10 |  | 0 |  |  |  | -5.5626e-10 |  |  |  | -1.3907e-10
Solution 2 | stage0 | Gas | Import | hub13 | 0 | -1.0679e-11 | -6.494e-13 |  | -1.0679e-11 |  | 0 |  |  |  | -4.6386e-11 |  |  |  | -1.1596e-11
Solution 2 | stage0 | Gas | Import | hub5 | 0 | -1.8391e-11 | -1.1184e-12 |  | -1.8391e-11 |  | 0 |  |  |  | -7.9888e-11 |  |  |  | -1.9972e-11
Solution 2 | stage0 | Gas | Import | hub9 | 0 | -9.9774e-11 | -6.0676e-12 |  | -9.9774e-11 |  | 0 |  |  |  | -4.334e-10 |  |  |  | -1.0835e-10
Solution 2 | stage0 | Gas | Import | hub12 | 0 | -1.1974e-09 | -7.2819e-11 |  | -1.1974e-09 |  | 0 |  |  |  | -5.2013e-09 |  |  |  | -1.3003e-09
Solution 2 | stage0 | Heat ambient in | Import | plant | 0 | 0 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0
Solution 2 | stage0 | Electricity | Import | hub10 | 34.5973 | 104102.8996 | 6330.8579 |  | 104102.8996 |  | 0 |  |  |  | 187311.5986 |  |  |  | 43730.1641
Solution 2 | stage0 | Electricity | Import | plant | 360.6814 | 2244018.6605 | 136466.5477 |  | 2244018.6605 |  | 0 |  |  |  | 5039307.0827 |  |  |  | 1123880.7842
Solution 2 | stage0 | Electricity | Import | hub8 | 188.2815 | 609822.6911 | 37085.4302 |  | 609822.6911 |  | 0 |  |  |  | 1187368.5647 |  |  |  | 232639.4666
Solution 2 | stage0 | Electricity | Import | hub11 | 160.8568 | 707617.8345 | 43032.6916 |  | 707617.8345 |  | 0 |  |  |  | 1416616.1541 |  |  |  | 292582.2931
Solution 2 | stage0 | Electricity | Import | hub7 | 187.8 | 669749.7981 | 40729.8051 |  | 669749.7981 |  | 0 |  |  |  | 1261496.0329 |  |  |  | 254894.9404
Solution 2 | stage0 | Electricity | Import | hub14 | 53.1154 | 268174.8955 | 16308.6443 |  | 268174.8955 |  | 0 |  |  |  | 464589.3211 |  |  |  | 108537.2486
Solution 2 | stage0 | Electricity | Import | hub2 | 137.9834 | 644617.8585 | 39201.4448 |  | 644617.8585 |  | 0 |  |  |  | 1072266.0433 |  |  |  | 259137.5746
Solution 2 | stage0 | Electricity | Import | hub3 | 85.7656 | 758032.3037 | 46098.5701 |  | 758032.3037 |  | 0 |  |  |  | 1334276.6005 |  |  |  | 304119.2277
Solution 2 | stage0 | Electricity | Import | hub4 | 486.8672 | 2333488.9581 | 141907.5464 |  | 2333488.9581 |  | 0 |  |  |  | 4039246.9821 |  |  |  | 904563.6738
Solution 2 | stage0 | Electricity | Import | hub6 | 23.418 | 43394.1192 | 2638.9467 |  | 43394.1192 |  | 0 |  |  |  | 68527.6056 |  |  |  | 18572.928
Solution 2 | stage0 | Electricity | Import | hub1 | 1375.5609 | 6456819.1812 | 392661.5398 |  | 6456819.1812 |  | 0 |  |  |  | 9651402.7298 |  |  |  | 2582709.0745
Solution 2 | stage0 | Electricity | Import | hub13 | 71.9467 | 201384.4438 | 12246.8856 |  | 201384.4438 |  | 0 |  |  |  | 354297.8734 |  |  |  | 85823.9603
Solution 2 | stage0 | Electricity | Import | hub5 | 276.9865 | 1356151.6683 | 82472.2804 |  | 1356151.6683 |  | 0 |  |  |  | 2341543.3461 |  |  |  | 525209.1794
Solution 2 | stage0 | Electricity | Import | hub9 | 671.0256 | 5851427.0176 | 355845.5454 |  | 5851427.0176 |  | 0 |  |  |  | 9779313.4589 |  |  |  | 2332820.9897
Solution 2 | stage0 | Electricity | Import | hub12 | 2041.802 | 20238400.1332 | 1230767.2147 |  | 20238400.1332 |  | 0 |  |  |  | 37103428.0706 |  |  |  | 8180837.2747
Solution 2 | stage0 | Slack | Export | hub10 | 0.30656 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 83.9112
Solution 2 | stage0 | Slack | Export | hub8 | 0.56463 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 229.337
Solution 2 | stage0 | Slack | Export | hub11 | 0.61341 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 503.439
Solution 2 | stage0 | Slack | Export | hub7 | 0.5632 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 247.8541
Solution 2 | stage0 | Slack | Export | hub14 | 0.4369 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 216.1531
Solution 2 | stage0 | Slack | Export | hub2 | 1.1052 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 140.1187
Solution 2 | stage0 | Slack | Export | hub3 | 0.29564 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 79.1189
Solution 2 | stage0 | Slack | Export | hub4 | 1.4166 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 610.4638
Solution 2 | stage0 | Slack | Export | hub6 | 0.44146 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 106.3182
Solution 2 | stage0 | Slack | Export | hub1 | 8.8973 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 768.9166
Solution 2 | stage0 | Slack | Export | hub13 | 0.47613 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 120.3074
Solution 2 | stage0 | Slack | Export | hub5 | 0.78215 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 296.7717
Solution 2 | stage0 | Slack | Export | hub9 | 3.0121 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 969.1649
Solution 2 | stage0 | Slack | Export | hub12 | 3.8336 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 10908.0949
Solution 2 | stage0 | Heat ambient out | Export | plant | 1288.1478 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 7118728.2661
Solution 2 | stage0 | export_electricity | Export | plant | 831.7176 | -20806.6428 | -1265.324 |  |  | 20806.6428 | 0 |  |  |  |  | 0 |  |  |  | 42177.4674
Solution 2 | stage0 | parking to pv | Conversion | plant | 0.1 | 411.3186 | 25.0137 | 400 |  |  | 65.7749 | 0 | 54.4563 | 0 |  |  | 25 |  | 132.034 | 132.034
Solution 2 | stage0 | cooling tower plant | Conversion | plant | 1288.1478 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 7118728.2661 | 7118728.2661
Solution 2 | stage0 | pv to hub | Conversion | hub1 | 815.2307 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 631219.3732 | 631219.3732
Solution 2 | stage0 | pv to hub | Conversion | hub10 | 19.0762 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 35129.883 | 35129.883
Solution 2 | stage0 | pv to hub | Conversion | hub11 | 112.6625 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 265718.2244 | 265718.2244
Solution 2 | stage0 | pv to hub | Conversion | hub12 | 1539.7145 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 2512423.6844 | 2512423.6844
Solution 2 | stage0 | pv to hub | Conversion | hub13 | 14.2794 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 19333.9627 | 19333.9627
Solution 2 | stage0 | pv to hub | Conversion | hub14 | 12.1921 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 24839.5804 | 24839.5804
Solution 2 | stage0 | pv to hub | Conversion | hub2 | 73.8767 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 72295.944 | 72295.944
Solution 2 | stage0 | pv to hub | Conversion | hub3 | 62.3084 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 139531.2739 | 139531.2739
Solution 2 | stage0 | pv to hub | Conversion | hub4 | 143.4758 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 36378.7836 | 36378.7836
Solution 2 | stage0 | pv to hub | Conversion | hub5 | 79.0594 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 10901.6657 | 10901.6657
Solution 2 | stage0 | pv to hub | Conversion | hub6 | 71.9101 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 47964.0919 | 47964.0919
Solution 2 | stage0 | pv to hub | Conversion | hub7 | 57.1823 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 93121.4141 | 93121.4141
Solution 2 | stage0 | pv to hub | Conversion | hub8 | 60.1299 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 122272.5785 | 122272.5785
Solution 2 | stage0 | pv to hub | Conversion | hub9 | 330.3086 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 138690.196 | 138690.196
Solution 2 | stage0 | pv to electricity | Conversion | plant | 321.6684 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 288544.7947 | 288544.7947
Solution 2 | stage0 | Pump DHW gas | Conversion | hub1 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 2 | stage0 | Pump DHW gas | Conversion | hub10 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 2 | stage0 | Pump DHW gas | Conversion | hub11 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 2 | stage0 | Pump DHW gas | Conversion | hub12 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 2 | stage0 | Pump DHW gas | Conversion | hub13 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 2 | stage0 | Pump DHW gas | Conversion | hub14 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 2 | stage0 | Pump DHW gas | Conversion | hub2 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 2 | stage0 | Pump DHW gas | Conversion | hub3 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 2 | stage0 | Pump DHW gas | Conversion | hub4 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 2 | stage0 | Pump DHW gas | Conversion | hub5 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 2 | stage0 | Pump DHW gas | Conversion | hub6 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 2 | stage0 | Pump DHW gas | Conversion | hub7 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 2 | stage0 | Pump DHW gas | Conversion | hub8 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 2 | stage0 | Pump DHW gas | Conversion | hub9 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 2 | stage0 | HEX pump ETS | Conversion | hub1 | 1506.007 | 1009648.2876 | 61400.2096 | 759776.9816 |  |  | 249871.306 | 0 | 0 | 0 |  |  | 20 |  | 381515.651 | 381515.651
Solution 2 | stage0 | HEX pump ETS | Conversion | hub10 | 106.6678 | 479677.6208 | 29170.8577 | 360965.3177 |  |  | 118712.3031 | 0 | 0 | 0 |  |  | 20 |  | 41908.9843 | 41908.9843
Solution 2 | stage0 | HEX pump ETS | Conversion | hub11 | 167.2098 | 502606.647 | 30565.2512 | 378219.7879 |  |  | 124386.8591 | 0 | 0 | 0 |  |  | 20 |  | 247254.7095 | 247254.7095
Solution 2 | stage0 | HEX pump ETS | Conversion | hub12 | 1916.8039 | 1165229.1204 | 70861.619 | 876854.1232 |  |  | 288374.9972 | 0 | 0 | 0 |  |  | 20 |  | 5454047.471 | 5454047.471
Solution 2 | stage0 | HEX pump ETS | Conversion | hub13 | 104.4963 | 478855.2105 | 29120.844 | 360346.4403 |  |  | 118508.7701 | 0 | 0 | 0 |  |  | 20 |  | 58235.8836 | 58235.8836
Solution 2 | stage0 | HEX pump ETS | Conversion | hub14 | 107.4477 | 479972.9898 | 29188.8201 | 361187.5877 |  |  | 118785.4021 | 0 | 0 | 0 |  |  | 20 |  | 107965.5397 | 107965.5397
Solution 2 | stage0 | HEX pump ETS | Conversion | hub2 | 202.6796 | 516040.1028 | 31382.1861 | 388328.6849 |  |  | 127711.418 | 0 | 0 | 0 |  |  | 20 |  | 68565.2984 | 68565.2984
Solution 2 | stage0 | HEX pump ETS | Conversion | hub3 | 40.274 | 454532.3358 | 27641.6858 | 342043.0762 |  |  | 112489.2596 | 0 | 0 | 0 |  |  | 20 |  | 35620.6064 | 35620.6064
Solution 2 | stage0 | HEX pump ETS | Conversion | hub4 | 185.968 | 509710.9482 | 30997.2883 | 383565.8917 |  |  | 126145.0565 | 0 | 0 | 0 |  |  | 20 |  | 283627.9397 | 283627.9397
Solution 2 | stage0 | HEX pump ETS | Conversion | hub5 | 89.6684 | 473239.4412 | 28779.3296 | 356120.4814 |  |  | 117118.9598 | 0 | 0 | 0 |  |  | 20 |  | 136885.5619 | 136885.5619
Solution 2 | stage0 | HEX pump ETS | Conversion | hub6 | 83.8601 | 471039.6701 | 28645.5539 | 354465.1173 |  |  | 116574.5527 | 0 | 0 | 0 |  |  | 20 |  | 52611.6329 | 52611.6329
Solution 2 | stage0 | HEX pump ETS | Conversion | hub7 | 69.4998 | 465601.0019 | 28314.8097 | 350372.4299 |  |  | 115228.572 | 0 | 0 | 0 |  |  | 20 |  | 115772.3768 | 115772.3768
Solution 2 | stage0 | HEX pump ETS | Conversion | hub8 | 66.7487 | 464559.079 | 28251.4468 | 349588.3658 |  |  | 114970.7133 | 0 | 0 | 0 |  |  | 20 |  | 105651.9546 | 105651.9546
Solution 2 | stage0 | HEX pump ETS | Conversion | hub9 | 463.7871 | 614929.1318 | 37395.9705 | 462744.3095 |  |  | 152184.8223 | 0 | 0 | 0 |  |  | 20 |  | 480182.9206 | 480182.9206
Solution 2 | stage0 | Main HP | Conversion | plant | 1159.333 | 2512731.8942 | 152807.9302 | 1890872.1756 |  |  | 621859.7186 | 0 | 0 | 0 |  |  | 20 |  | 6406855.4395 | 6406855.4395
Solution 2 | stage0 | Pump cooling | Conversion | hub1 | 2746.524 | 171158.67 | 10408.7516 | 128799.7209 |  |  | 42358.9491 | 0 | 0 | 0 |  |  | 20 |  | 2915759.2445 | 2915759.2445
Solution 2 | stage0 | Pump cooling | Conversion | hub10 | 43.5653 | 63401.8789 | 3855.6879 | 47710.9591 |  |  | 15690.9198 | 0 | 0 | 0 |  |  | 20 |  | 40007.4138 | 40007.4138
Solution 2 | stage0 | Pump cooling | Conversion | hub11 | 266.7618 | 72299.8815 | 4396.8062 | 54406.8527 |  |  | 17893.0287 | 0 | 0 | 0 |  |  | 20 |  | 591625.2592 | 591625.2592
Solution 2 | stage0 | Pump cooling | Conversion | hub12 | 4679.9342 | 248236.4561 | 15096.1187 | 186802.0256 |  |  | 61434.4304 | 0 | 0 | 0 |  |  | 20 |  | 9316324.8382 | 9316324.8382
Solution 2 | stage0 | Pump cooling | Conversion | hub13 | 151.9881 | 67724.2879 | 4118.5485 | 50963.6432 |  |  | 16760.6448 | 0 | 0 | 0 |  |  | 20 |  | 69307.0831 | 69307.0831
Solution 2 | stage0 | Pump cooling | Conversion | hub14 | 103.6616 | 65797.6909 | 4001.3855 | 49513.8471 |  |  | 16283.8437 | 0 | 0 | 0 |  |  | 20 |  | 51168.1813 | 51168.1813
Solution 2 | stage0 | Pump cooling | Conversion | hub2 | 326.6423 | 74687.0943 | 4541.9809 | 56203.2698 |  |  | 18483.8245 | 0 | 0 | 0 |  |  | 20 |  | 228166.8433 | 228166.8433
Solution 2 | stage0 | Pump cooling | Conversion | hub3 | 100.4378 | 65669.1709 | 3993.5697 | 49417.1337 |  |  | 16252.0372 | 0 | 0 | 0 |  |  | 20 |  | 131510.3058 | 131510.3058
Solution 2 | stage0 | Pump cooling | Conversion | hub4 | 748.031 | 91486.2748 | 5563.5973 | 68844.9301 |  |  | 22641.3448 | 0 | 0 | 0 |  |  | 20 |  | 811707.9698 | 811707.9698
Solution 2 | stage0 | Pump cooling | Conversion | hub5 | 380.9923 | 76853.8252 | 4673.7473 | 57833.7705 |  |  | 19020.0547 | 0 | 0 | 0 |  |  | 20 |  | 422265.8725 | 422265.8725
Solution 2 | stage0 | Pump cooling | Conversion | hub6 | 127.8045 | 66760.1774 | 4059.9176 | 50238.1341 |  |  | 16522.0433 | 0 | 0 | 0 |  |  | 20 |  | 33799.1385 | 33799.1385
Solution 2 | stage0 | Pump cooling | Conversion | hub7 | 264.3832 | 72205.0571 | 4391.0396 | 54335.4958 |  |  | 17869.5612 | 0 | 0 | 0 |  |  | 20 |  | 292396.6081 | 292396.6081
Solution 2 | stage0 | Pump cooling | Conversion | hub8 | 267.1967 | 72317.22 | 4397.8606 | 54419.9003 |  |  | 17897.3197 | 0 | 0 | 0 |  |  | 20 |  | 309788.5739 | 309788.5739
Solution 2 | stage0 | Pump cooling | Conversion | hub9 | 1086.2268 | 104968.8674 | 6383.5204 | 78990.8032 |  |  | 25978.0642 | 0 | 0 | 0 |  |  | 20 |  | 1693852.2016 | 1693852.2016
Solution 2 | stage0 | Pump DHW | Conversion | hub1 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 2 | stage0 | Pump DHW | Conversion | hub10 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 2 | stage0 | Pump DHW | Conversion | hub11 | 34.8297 | 8790.9289 | 534.6068 | 6615.3189 |  |  | 2175.61 | 0 | 0 | 0 |  |  | 20 |  | 157809.6407 | 157809.6407
Solution 2 | stage0 | Pump DHW | Conversion | hub12 | 554.1475 | 11551.3616 | 702.4783 | 8692.59 |  |  | 2858.7716 | 0 | 0 | 0 |  |  | 20 |  | 3432869.3219 | 3432869.3219
Solution 2 | stage0 | Pump DHW | Conversion | hub13 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 2 | stage0 | Pump DHW | Conversion | hub14 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 2 | stage0 | Pump DHW | Conversion | hub2 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 2 | stage0 | Pump DHW | Conversion | hub3 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 2 | stage0 | Pump DHW | Conversion | hub4 | 94.6748 | 9109.0353 | 553.952 | 6854.6992 |  |  | 2254.3361 | 0 | 0 | 0 |  |  | 20 |  | 355179.8886 | 355179.8886
Solution 2 | stage0 | Pump DHW | Conversion | hub5 | 55.1879 | 8899.1428 | 541.1877 | 6696.7517 |  |  | 2202.3911 | 0 | 0 | 0 |  |  | 20 |  | 207042.1928 | 207042.1928
Solution 2 | stage0 | Pump DHW | Conversion | hub6 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 2 | stage0 | Pump DHW | Conversion | hub7 | 43.6957 | 8838.056 | 537.4728 | 6650.7829 |  |  | 2187.2732 | 0 | 0 | 0 |  |  | 20 |  | 163928.5463 | 163928.5463
Solution 2 | stage0 | Pump DHW | Conversion | hub8 | 43.6957 | 8838.056 | 537.4728 | 6650.7829 |  |  | 2187.2732 | 0 | 0 | 0 |  |  | 20 |  | 163928.5463 | 163928.5463
Solution 2 | stage0 | Pump DHW | Conversion | hub9 | 71.4402 | 8985.5316 | 546.4413 | 6761.7607 |  |  | 2223.7709 | 0 | 0 | 0 |  |  | 20 |  | 268013.7936 | 268013.7936
Solution 2 | stage0 | Pump SH | Conversion | hub1 | 2304.5377 | 203386.154 | 12368.6165 | 153051.434 |  |  | 50334.7201 | 0 | 0 | 0 |  |  | 20 |  | 769002.1132 | 769002.1132
Solution 2 | stage0 | Pump SH | Conversion | hub10 | 135.9123 | 93876.5701 | 5708.9594 | 70643.6666 |  |  | 23232.9034 | 0 | 0 | 0 |  |  | 20 |  | 51886.8029 | 51886.8029
Solution 2 | stage0 | Pump SH | Conversion | hub11 | 218.5355 | 98048.8117 | 5962.6879 | 73783.3473 |  |  | 24265.4645 | 0 | 0 | 0 |  |  | 20 |  | 358030.5729 | 358030.5729
Solution 2 | stage0 | Pump SH | Conversion | hub12 | 2153.8699 | 195777.846 | 11905.929 | 147326.0568 |  |  | 48451.7893 | 0 | 0 | 0 |  |  | 20 |  | 7345736.8521 | 7345736.8521
Solution 2 | stage0 | Pump SH | Conversion | hub13 | 140.401 | 94103.2358 | 5722.7437 | 70814.2363 |  |  | 23288.9995 | 0 | 0 | 0 |  |  | 20 |  | 72255.5737 | 72255.5737
Solution 2 | stage0 | Pump SH | Conversion | hub14 | 142.1925 | 94193.7038 | 5728.2454 | 70882.315 |  |  | 23311.3888 | 0 | 0 | 0 |  |  | 20 |  | 133678.2323 | 133678.2323
Solution 2 | stage0 | Pump SH | Conversion | hub2 | 279.8181 | 101143.4144 | 6150.8814 | 76112.0868 |  |  | 25031.3276 | 0 | 0 | 0 |  |  | 20 |  | 85065.6119 | 85065.6119
Solution 2 | stage0 | Pump SH | Conversion | hub3 | 58.7399 | 89979.5802 | 5471.9699 | 67711.1175 |  |  | 22268.4627 | 0 | 0 | 0 |  |  | 20 |  | 44423.8362 | 44423.8362
Solution 2 | stage0 | Pump SH | Conversion | hub4 | 273.5294 | 100825.8515 | 6131.5693 | 75873.1155 |  |  | 24952.736 | 0 | 0 | 0 |  |  | 20 |  | 263452.5885 | 263452.5885
Solution 2 | stage0 | Pump SH | Conversion | hub5 | 136.167 | 93889.4307 | 5709.7415 | 70653.3444 |  |  | 23236.0862 | 0 | 0 | 0 |  |  | 20 |  | 116315.6148 | 116315.6148
Solution 2 | stage0 | Pump SH | Conversion | hub6 | 115.1239 | 92826.813 | 5645.12 | 69853.7071 |  |  | 22973.1059 | 0 | 0 | 0 |  |  | 20 |  | 65178.3221 | 65178.3221
Solution 2 | stage0 | Pump SH | Conversion | hub7 | 104.0534 | 92267.7852 | 5611.1236 | 69433.0295 |  |  | 22834.7557 | 0 | 0 | 0 |  |  | 20 |  | 100816.5425 | 100816.5425
Solution 2 | stage0 | Pump SH | Conversion | hub8 | 100.9653 | 92111.8452 | 5601.6404 | 69315.682 |  |  | 22796.1631 | 0 | 0 | 0 |  |  | 20 |  | 97713.9952 | 97713.9952
Solution 2 | stage0 | Pump SH | Conversion | hub9 | 674.3585 | 121066.6146 | 7362.4802 | 91104.6234 |  |  | 29961.9912 | 0 | 0 | 0 |  |  | 20 |  | 577006.576 | 577006.576
Solution 2 | stage0 | HEX SC ets | Conversion | hub1 | 8.8973 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 768916.582 | 768.9166
Solution 2 | stage0 | HEX SC ets | Conversion | hub10 | 0.30656 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 83911.1943 | 83.9112
Solution 2 | stage0 | HEX SC ets | Conversion | hub11 | 0.61341 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 503439.03 | 503.439
Solution 2 | stage0 | HEX SC ets | Conversion | hub12 | 3.8336 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 10908094.9421 | 10908.0949
Solution 2 | stage0 | HEX SC ets | Conversion | hub13 | 0.47613 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 120307.3634 | 120.3074
Solution 2 | stage0 | HEX SC ets | Conversion | hub14 | 0.4369 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 216153.0828 | 216.1531
Solution 2 | stage0 | HEX SC ets | Conversion | hub2 | 1.1052 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 140118.6621 | 140.1187
Solution 2 | stage0 | HEX SC ets | Conversion | hub3 | 0.29564 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 79118.8592 | 79.1189
Solution 2 | stage0 | HEX SC ets | Conversion | hub4 | 1.4166 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 610463.826 | 610.4638
Solution 2 | stage0 | HEX SC ets | Conversion | hub5 | 0.78215 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 296771.6551 | 296.7717
Solution 2 | stage0 | HEX SC ets | Conversion | hub6 | 0.44146 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 106318.2183 | 106.3182
Solution 2 | stage0 | HEX SC ets | Conversion | hub7 | 0.5632 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 247854.1085 | 247.8541
Solution 2 | stage0 | HEX SC ets | Conversion | hub8 | 0.56463 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 229336.9551 | 229.337
Solution 2 | stage0 | HEX SC ets | Conversion | hub9 | 3.0121 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 969164.8914 | 969.1649
Solution 2 | stage0 | ETS HP | Conversion | hub1 | 2942.74 | 8160047.4971 | 496240.7534 | 6140570.2691 |  |  | 2019477.228 | 0 | 0 | 0 |  |  | 20 |  | 191368.5124 | 2870474.2955
Solution 2 | stage0 | ETS HP | Conversion | hub10 | 46.7128 | 155257.2966 | 9441.734 | 116833.6753 |  |  | 38423.6213 | 0 | 0 | 0 |  |  | 20 |  | 2864.7809 | 42923.9925
Solution 2 | stage0 | ETS HP | Conversion | hub11 | 308.2411 | 878136.8706 | 53402.5448 | 660812.4722 |  |  | 217324.3984 | 0 | 0 | 0 |  |  | 20 |  | 66663.3193 | 655295.0297
Solution 2 | stage0 | ETS HP | Conversion | hub12 | 5310.3877 | 14704365.3212 | 894223.3888 | 11065277.3222 |  |  | 3639087.999 | 0 | 0 | 0 |  |  | 20 |  | 1208378.3477 | 10780202.7533
Solution 2 | stage0 | ETS HP | Conversion | hub13 | 162.8801 | 476350.5423 | 28968.5265 | 358461.6362 |  |  | 117888.906 | 0 | 0 | 0 |  |  | 20 |  | 5082.5008 | 76187.9508
Solution 2 | stage0 | ETS HP | Conversion | hub14 | 111.1017 | 333231.9035 | 20264.9863 | 250762.5011 |  |  | 82469.4024 | 0 | 0 | 0 |  |  | 20 |  | 3664.3965 | 54940.7582
Solution 2 | stage0 | ETS HP | Conversion | hub2 | 350.0096 | 993587.5886 | 60423.5029 | 747691.0408 |  |  | 245896.5478 | 0 | 0 | 0 |  |  | 20 |  | 16397.0287 | 245919.9142
Solution 2 | stage0 | ETS HP | Conversion | hub3 | 107.6476 | 323684.7024 | 19684.3879 | 243578.0749 |  |  | 80106.6275 | 0 | 0 | 0 |  |  | 20 |  | 9666.0202 | 144867.2684
Solution 2 | stage0 | ETS HP | Conversion | hub4 | 890.3732 | 2487184.2906 | 151254.2919 | 1871647.1827 |  |  | 615537.1079 | 0 | 0 | 0 |  |  | 20 |  | 127661.1303 | 1112094.6177
Solution 2 | stage0 | ETS HP | Conversion | hub5 | 454.7032 | 1282966.6758 | 78021.6475 | 965453.5747 |  |  | 317513.1011 | 0 | 0 | 0 |  |  | 20 |  | 70546.0573 | 593699.6509
Solution 2 | stage0 | ETS HP | Conversion | hub6 | 136.9691 | 404730.9017 | 24613.0881 | 304566.676 |  |  | 100164.2257 | 0 | 0 | 0 |  |  | 20 |  | 2454.4302 | 36772.9943
Solution 2 | stage0 | ETS HP | Conversion | hub7 | 320.1752 | 911123.4647 | 55408.5739 | 685635.4281 |  |  | 225488.0366 | 0 | 0 | 0 |  |  | 20 |  | 52846.3343 | 424555.2293
Solution 2 | stage0 | ETS HP | Conversion | hub8 | 325.5675 | 926028.1552 | 56314.9797 | 696851.4534 |  |  | 229176.7018 | 0 | 0 | 0 |  |  | 20 |  | 53846.5729 | 436500.5832
Solution 2 | stage0 | ETS HP | Conversion | hub9 | 1231.3486 | 3429660.659 | 208569.5445 | 2580876.1877 |  |  | 848784.4713 | 0 | 0 | 0 |  |  | 20 |  | 172249.6659 | 1948195.4902
Solution 2 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub1 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -2.2397e-11 | -2.0157e-11
Solution 2 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub10 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -1.7615e-12 | -1.5854e-12
Solution 2 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub11 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -1.3512e-11 | -1.216e-11
Solution 2 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub12 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -2.8422e-10 | -2.558e-10
Solution 2 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub13 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -2.2172e-12 | -1.9955e-12
Solution 2 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub14 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -5.6267e-12 | -5.064e-12
Solution 2 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub2 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -3.0027e-12 | -2.7024e-12
Solution 2 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub3 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -2.4866e-12 | -2.238e-12
Solution 2 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub4 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -7.8906e-12 | -7.1015e-12
Solution 2 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub5 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -4.184e-12 | -3.7656e-12
Solution 2 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub6 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -2.3913e-12 | -2.1521e-12
Solution 2 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub7 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -3.4385e-12 | -3.0947e-12
Solution 2 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub8 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -3.0713e-12 | -2.7642e-12
Solution 2 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub9 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -2.3405e-11 | -2.1065e-11
Solution 2 | stage0 | rooftop to pv | Conversion | plant | 3393.3764 | 12212888.5564 | 742708.0566 | 11876817.3281 |  |  | 1952991.4229 | 0 | 1616920.1946 | 0 |  |  | 25 |  | 4480410.8838 | 4480410.8838
Solution 2 | stage0 | battery | Storage | plant | 0.1 | 98.0774 | 5.9644 | 75.7 |  |  | 0 | 56.7303 | 34.3529 | 0 |  |  | 15 |  | 73.6681 | 73.6681
Solution 2 | stage0 | Generic Hot Water Storage hub1 | Storage | hub1 | 0.27028 | 14948.9498 | 909.0974 | 13813.2437 |  |  | 1135.706 | 0 | 0 | 0 |  |  | 20 |  | 26.6951 | 0
Solution 2 | stage0 | Generic Hot Water Storage hub2 | Storage | hub2 | 0.18177 | 14944.2563 | 908.812 | 13808.9069 |  |  | 1135.3495 | 0 | 0 | 0 |  |  | 20 |  | 17.758 | 0
Solution 2 | stage0 | Generic Hot Water Storage hub3 | Storage | hub3 | 0.6601 | 14969.6216 | 910.3545 | 13832.3451 |  |  | 1137.2765 | 0 | 0 | 0 |  |  | 20 |  | 61.5175 | 0
Solution 2 | stage0 | Generic Hot Water Storage hub4 | Storage | hub4 | 524.9076 | 42769.7936 | 2600.9793 | 39520.4742 |  |  | 3249.3195 | 0 | 0 | 0 |  |  | 20 |  | 180843.4822 | 134612.2022
Solution 2 | stage0 | Generic Hot Water Storage hub5 | Storage | hub5 | 285.4266 | 30070.4226 | 1828.6866 | 27785.9036 |  |  | 2284.5191 | 0 | 0 | 0 |  |  | 20 |  | 100472.7484 | 75269.3366
Solution 2 | stage0 | Generic Hot Water Storage hub6 | Storage | hub6 | 0.26712 | 14948.7824 | 909.0872 | 13813.0891 |  |  | 1135.6933 | 0 | 0 | 0 |  |  | 20 |  | 21.7292 | 0
Solution 2 | stage0 | Generic Hot Water Storage hub7 | Storage | hub7 | 234.2861 | 27358.5072 | 1663.7656 | 25280.0185 |  |  | 2078.4886 | 0 | 0 | 0 |  |  | 20 |  | 80205.7916 | 60064.445
Solution 2 | stage0 | Generic Hot Water Storage hub8 | Storage | hub8 | 249.0893 | 28143.4997 | 1711.5037 | 26005.3734 |  |  | 2138.1263 | 0 | 0 | 0 |  |  | 20 |  | 84032.5762 | 62362.1172
Solution 2 | stage0 | Generic Hot Water Storage hub9 | Storage | hub9 | 566.0698 | 44952.5703 | 2733.7215 | 41537.4203 |  |  | 3415.15 | 0 | 0 | 0 |  |  | 20 |  | 164066.0938 | 114305.1381
Solution 2 | stage0 | Generic Hot Water Storage hub10 | Storage | hub10 | 0.29546 | 14950.2853 | 909.1786 | 13814.4778 |  |  | 1135.8075 | 0 | 0 | 0 |  |  | 20 |  | 23.8608 | 0
Solution 2 | stage0 | Generic Hot Water Storage hub11 | Storage | hub11 | 180.8518 | 24524.9533 | 1491.4474 | 22661.7363 |  |  | 1863.217 | 0 | 0 | 0 |  |  | 20 |  | 62713.7612 | 48196.0222
Solution 2 | stage0 | Generic Hot Water Storage hub12 | Storage | hub12 | 3173.3607 | 183213.8532 | 11141.869 | 169294.676 |  |  | 13919.1772 | 0 | 0 | 0 |  |  | 20 |  | 1167531.1498 | 927664.2409
Solution 2 | stage0 | Generic Hot Water Storage hub13 | Storage | hub13 | 0.26628 | 14948.7376 | 909.0845 | 13813.0477 |  |  | 1135.6899 | 0 | 0 | 0 |  |  | 20 |  | 24.7809 | 0
Solution 2 | stage0 | Generic Hot Water Storage hub14 | Storage | hub14 | 0.15992 | 14943.0976 | 908.7415 | 13807.8361 |  |  | 1135.2614 | 0 | 0 | 0 |  |  | 20 |  | 12.5947 | 0
Solution 2 | stage0 | Generic Borehole | Storage | plant | 9500000 | 10571597.206 | 642895.4444 | 14250000 |  |  | 1171615.5519 | 0 | 4850018.3459 | 0 |  |  | 40 |  | 11166223.9238 | 9703240.4079
Solution 2 | stage0 | Anergy | Network | hub1_to_hub2_Anergy | 7736.5544 | 478628.6295 | 29107.0649 | 580800 |  |  | 95505.1667 | 0 | 197676.5372 | 0 |  |  | 40 | 528 | 6936029.5493 | 11536262.7835
Solution 2 | stage0 | Anergy | Network | hub3_to_hub4_Anergy | 7406.4203 | 452340.3146 | 27508.3814 | 548900 |  |  | 90259.6177 | 0 | 186819.3032 | 0 |  |  | 40 | 499 | 6845394.0936 | 11152054.6863
Solution 2 | stage0 | Anergy | Network | hub5_to_hub6_Anergy | 6508.4723 | 317272.7657 | 19294.4559 | 385000 |  |  | 63308.3491 | 0 | 131035.5834 | 0 |  |  | 40 | 350 | 6446388.8266 | 10097374.9486
Solution 2 | stage0 | Anergy | Network | hub7_to_hub8_Anergy | 6240.8371 | 180392.2297 | 10970.2763 | 218900 |  |  | 35995.3185 | 0 | 74503.0888 | 0 |  |  | 40 | 199 | 6284048.4551 | 9823789.04
Solution 2 | stage0 | Anergy | Network | hub9_to_hub10_Anergy | 5029.6457 | 758735.1569 | 46141.313 | 920700 |  |  | 151397.3949 | 0 | 313362.238 | 0 |  |  | 40 | 837 | 5750503.5518 | 7945631.8367
Solution 2 | stage0 | Anergy | Network | hub11_to_hub12_Anergy | 4745.1749 | 591940.3315 | 35997.9419 | 718300 |  |  | 118115.2914 | 0 | 244474.9598 | 0 |  |  | 40 | 653 | 5479254.6582 | 7421593.0692
Solution 2 | stage0 | Anergy | Network | hub13_to_hub14_Anergy | 113.8479 | 383446.7997 | 23318.7281 | 465300 |  |  | 76512.6619 | 0 | 158365.8622 | 0 |  |  | 40 | 423 | 105266.4012 | 56222.73
Solution 2 | stage0 | pv_loop | Network | hub1_to_hub2_pv_loop | 2262.8414 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 528 | 3518601.2825 | 0
Solution 2 | stage0 | pv_loop | Network | hub3_to_hub4_pv_loop | 2203.5115 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 499 | 3306774.0646 | 0
Solution 2 | stage0 | pv_loop | Network | hub5_to_hub6_pv_loop | 1985.0177 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 350 | 3259493.6153 | 0
Solution 2 | stage0 | pv_loop | Network | hub7_to_hub8_pv_loop | 1927.1374 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 199 | 3118408.1094 | 0
Solution 2 | stage0 | pv_loop | Network | hub9_to_hub10_pv_loop | 1622.6446 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 837 | 2857445.3349 | 0
Solution 2 | stage0 | pv_loop | Network | hub11_to_hub12_pv_loop | 1540.416 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 653 | 2556597.2275 | 0
Solution 2 | stage0 | pv_loop | Network | hub13_to_hub14_pv_loop | 12.1921 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 423 | 24839.5804 | 0
Solution 2 | stage0 | Anergy | Network | plant_to_hub1_Anergy | 10492.0879 | 94275.3361 | 5733.2097 | 114400 |  |  | 18811.6237 | 0 | 38936.2876 | 0 |  |  | 40 | 104 | 7103874.0756 | 14273160.2787
Solution 2 | stage0 | Anergy | Network | hub2_to_hub3_Anergy | 7516.005 | 109685.7276 | 6670.369 | 133100 |  |  | 21886.6007 | 0 | 45300.8731 | 0 |  |  | 40 | 121 | 6879532.3908 | 11295941.7924
Solution 2 | stage0 | Anergy | Network | hub4_to_hub5_Anergy | 6748.5523 | 119657.1574 | 7276.7662 | 145200 |  |  | 23876.2917 | 0 | 49419.1343 | 0 |  |  | 40 | 132 | 6576751.402 | 10453201.0556
Solution 2 | stage0 | Anergy | Network | hub6_to_hub7_Anergy | 6415.7201 | 145945.4722 | 8875.4497 | 177100 |  |  | 29121.8406 | 0 | 60276.3684 | 0 |  |  | 40 | 161 | 6395726.0086 | 10060876.3815
Solution 2 | stage0 | Anergy | Network | hub8_to_hub9_Anergy | 6098.6229 | 1264558.5949 | 76902.1884 | 1534500 |  |  | 252328.9915 | 0 | 522270.3966 | 0 |  |  | 40 | 1395 | 6183346.1292 | 9578010.1339
Solution 2 | stage0 | Anergy | Network | hub10_to_hub11_Anergy | 4983.0873 | 144132.485 | 8765.1957 | 174900 |  |  | 28760.0786 | 0 | 59527.5936 | 0 |  |  | 40 | 159 | 5709671.9314 | 7901709.1489
Solution 2 | stage0 | Anergy | Network | hub12_to_hub13_Anergy | 228.6868 | 286451.9828 | 17420.1373 | 347600 |  |  | 57158.3952 | 0 | 118306.4124 | 0 |  |  | 40 | 316 | 162046.1162 | 132371.5577
Solution 2 | stage0 | pv_loop | Network | plant_to_hub1_pv_loop | 3071.708 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 104 | 4149820.6557 | 0
Solution 2 | stage0 | pv_loop | Network | hub2_to_hub3_pv_loop | 2239.6416 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 121 | 3446305.3385 | 0
Solution 2 | stage0 | pv_loop | Network | hub4_to_hub5_pv_loop | 2061.665 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 132 | 3270395.281 | 0
Solution 2 | stage0 | pv_loop | Network | hub6_to_hub7_pv_loop | 1982.9516 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 161 | 3211529.5235 | 0
Solution 2 | stage0 | pv_loop | Network | hub8_to_hub9_pv_loop | 1867.6478 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 1395 | 2996135.5309 | 0
Solution 2 | stage0 | pv_loop | Network | hub10_to_hub11_pv_loop | 1621.7903 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 159 | 2822315.4519 | 0
Solution 2 | stage0 | pv_loop | Network | hub12_to_hub13_pv_loop | 24.5549 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 316 | 44173.5431 | 0
Solution 3 | stage0 | Gas | Import | hub10 | 0 | -8.3142e-12 | -5.0561e-13 |  | -8.3142e-12 |  | 0 |  |  |  | -3.6115e-11 |  |  |  | -9.0288e-12
Solution 3 | stage0 | Gas | Import | hub8 | 0 | -2.1236e-11 | -1.2914e-12 |  | -2.1236e-11 |  | 0 |  |  |  | -9.2245e-11 |  |  |  | -2.3061e-11
Solution 3 | stage0 | Gas | Import | hub11 | 0 | -6.7433e-11 | -4.1009e-12 |  | -6.7433e-11 |  | 0 |  |  |  | -2.9292e-10 |  |  |  | -7.323e-11
Solution 3 | stage0 | Gas | Import | hub7 | 0 | -1.5011e-11 | -9.1287e-13 |  | -1.5011e-11 |  | 0 |  |  |  | -6.5205e-11 |  |  |  | -1.6301e-11
Solution 3 | stage0 | Gas | Import | hub14 | 0 | -2.1809e-11 | -1.3263e-12 |  | -2.1809e-11 |  | 0 |  |  |  | -9.4736e-11 |  |  |  | -2.3684e-11
Solution 3 | stage0 | Gas | Import | hub2 | 0 | -1.3348e-11 | -8.1174e-13 |  | -1.3348e-11 |  | 0 |  |  |  | -5.7981e-11 |  |  |  | -1.4495e-11
Solution 3 | stage0 | Gas | Import | hub3 | 0 | -8.7049e-12 | -5.2938e-13 |  | -8.7049e-12 |  | 0 |  |  |  | -3.7813e-11 |  |  |  | -9.4532e-12
Solution 3 | stage0 | Gas | Import | hub4 | 0 | -5.5027e-11 | -3.3464e-12 |  | -5.5027e-11 |  | 0 |  |  |  | -2.3903e-10 |  |  |  | -5.9756e-11
Solution 3 | stage0 | Gas | Import | hub6 | 0 | -1.4458e-11 | -8.7924e-13 |  | -1.4458e-11 |  | 0 |  |  |  | -6.2803e-11 |  |  |  | -1.5701e-11
Solution 3 | stage0 | Gas | Import | hub1 | 0 | -1.3359e-10 | -8.1239e-12 |  | -1.3359e-10 |  | 0 |  |  |  | -5.8028e-10 |  |  |  | -1.4507e-10
Solution 3 | stage0 | Gas | Import | hub13 | 0 | -1.7036e-11 | -1.036e-12 |  | -1.7036e-11 |  | 0 |  |  |  | -7.4003e-11 |  |  |  | -1.8501e-11
Solution 3 | stage0 | Gas | Import | hub5 | 0 | -1.8493e-11 | -1.1247e-12 |  | -1.8493e-11 |  | 0 |  |  |  | -8.0332e-11 |  |  |  | -2.0083e-11
Solution 3 | stage0 | Gas | Import | hub9 | 0 | -1.128e-10 | -6.8598e-12 |  | -1.128e-10 |  | 0 |  |  |  | -4.8999e-10 |  |  |  | -1.225e-10
Solution 3 | stage0 | Gas | Import | hub12 | 0.1 | -1.2104e-09 | -7.3608e-11 |  | -1.2104e-09 |  | 0 |  |  |  | -5.2577e-09 |  |  |  | -1.3144e-09
Solution 3 | stage0 | Heat ambient in | Import | plant | 0 | 0 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0
Solution 3 | stage0 | Electricity | Import | hub10 | 34.5973 | 57138.3714 | 3474.7823 |  | 57138.3714 |  | 0 |  |  |  | 126617.879 |  |  |  | 25589.321
Solution 3 | stage0 | Electricity | Import | plant | 375.4677 | 1627567.2723 | 98978.0035 |  | 1627567.2723 |  | 0 |  |  |  | 3737514.8047 |  |  |  | 793275.2943
Solution 3 | stage0 | Electricity | Import | hub8 | 138.2415 | 441618.4391 | 26856.347 |  | 441618.4391 |  | 0 |  |  |  | 959797.4426 |  |  |  | 180580.3392
Solution 3 | stage0 | Electricity | Import | hub11 | 136.9186 | 610899.176 | 37150.8949 |  | 610899.176 |  | 0 |  |  |  | 1248732.6589 |  |  |  | 256152.1914
Solution 3 | stage0 | Electricity | Import | hub7 | 138.6188 | 460508.848 | 28005.1382 |  | 460508.848 |  | 0 |  |  |  | 995618.8845 |  |  |  | 191396.4472
Solution 3 | stage0 | Electricity | Import | hub14 | 52.3005 | 121071.074 | 7362.7514 |  | 121071.074 |  | 0 |  |  |  | 264167.1247 |  |  |  | 55213.6291
Solution 3 | stage0 | Electricity | Import | hub2 | 137.9834 | 392979.2719 | 23898.4307 |  | 392979.2719 |  | 0 |  |  |  | 730716.8524 |  |  |  | 166767.2281
Solution 3 | stage0 | Electricity | Import | hub3 | 82.6327 | 578072.5757 | 35154.5957 |  | 578072.5757 |  | 0 |  |  |  | 1106567.4626 |  |  |  | 246573.5621
Solution 3 | stage0 | Electricity | Import | hub4 | 375.7377 | 1913301.6608 | 116354.5014 |  | 1913301.6608 |  | 0 |  |  |  | 3499362.1879 |  |  |  | 745256.8058
Solution 3 | stage0 | Electricity | Import | hub6 | 23.418 | 25372.4415 | 1542.9861 |  | 25372.4415 |  | 0 |  |  |  | 47757.7531 |  |  |  | 11019.3448
Solution 3 | stage0 | Electricity | Import | hub1 | 1375.5616 | 4647535.1927 | 282632.7134 |  | 4647535.1927 |  | 0 |  |  |  | 7458085.1948 |  |  |  | 1894656.2825
Solution 3 | stage0 | Electricity | Import | hub13 | 71.9467 | 100997.7735 | 6142.0244 |  | 100997.7735 |  | 0 |  |  |  | 214232.4028 |  |  |  | 45229.584
Solution 3 | stage0 | Electricity | Import | hub5 | 225.8713 | 1098230.006 | 66787.1708 |  | 1098230.006 |  | 0 |  |  |  | 2011889.8084 |  |  |  | 427185.5012
Solution 3 | stage0 | Electricity | Import | hub9 | 622.099 | 4782893.4643 | 290864.3187 |  | 4782893.4643 |  | 0 |  |  |  | 8425987.4715 |  |  |  | 1897394.1274
Solution 3 | stage0 | Electricity | Import | hub12 | 2033.7813 | 13367153.5859 | 812902.9113 |  | 13367153.5859 |  | 0 |  |  |  | 28206953.4449 |  |  |  | 5979176.1339
Solution 3 | stage0 | Slack | Export | hub10 | 0.30656 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 83.9195
Solution 3 | stage0 | Slack | Export | hub8 | 0.51751 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 226.3644
Solution 3 | stage0 | Slack | Export | hub11 | 0.59251 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 505.2353
Solution 3 | stage0 | Slack | Export | hub7 | 0.516 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 246.4714
Solution 3 | stage0 | Slack | Export | hub14 | 0.4369 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 216.1593
Solution 3 | stage0 | Slack | Export | hub2 | 1.1052 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 140.1317
Solution 3 | stage0 | Slack | Export | hub3 | 0.29564 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 79.1248
Solution 3 | stage0 | Slack | Export | hub4 | 1.3202 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 605.2105
Solution 3 | stage0 | Slack | Export | hub6 | 0.44146 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 106.3247
Solution 3 | stage0 | Slack | Export | hub1 | 8.8973 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 768.9228
Solution 3 | stage0 | Slack | Export | hub13 | 0.46855 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 119.6041
Solution 3 | stage0 | Slack | Export | hub5 | 0.65858 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 290.3236
Solution 3 | stage0 | Slack | Export | hub9 | 3.0999 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 972.6873
Solution 3 | stage0 | Slack | Export | hub12 | 4.0488 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 10893.2441
Solution 3 | stage0 | Heat ambient out | Export | plant | 1503.5918 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 7007857.6751
Solution 3 | stage0 | export_electricity | Export | plant | 2448.5161 | -273675.364 | -16643.1469 |  |  | 273675.364 | 0 |  |  |  |  | 0 |  |  |  | 554771.5618
Solution 3 | stage0 | parking to pv | Conversion | plant | 428.4382 | 1762246.0376 | 107168.2857 | 1713752.9896 |  |  | 281804.8638 | 0 | 233311.8159 | 0 |  |  | 25 |  | 565684.1953 | 565684.1953
Solution 3 | stage0 | cooling tower plant | Conversion | plant | 1503.5918 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 7007857.6751 | 7007857.6751
Solution 3 | stage0 | pv to hub | Conversion | hub1 | 1124.7082 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 1319272.4018 | 1319272.4018
Solution 3 | stage0 | pv to hub | Conversion | hub10 | 25.7761 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 53273.23 | 53273.23
Solution 3 | stage0 | pv to hub | Conversion | hub11 | 137.8182 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 302439.2779 | 302439.2779
Solution 3 | stage0 | pv to hub | Conversion | hub12 | 1831.8778 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 4725576.2346 | 4725576.2346
Solution 3 | stage0 | pv to hub | Conversion | hub13 | 38.7899 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 59903.9319 | 59903.9319
Solution 3 | stage0 | pv to hub | Conversion | hub14 | 58.1681 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 78165.1388 | 78165.1388
Solution 3 | stage0 | pv to hub | Conversion | hub2 | 96.0606 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 164674.4894 | 164674.4894
Solution 3 | stage0 | pv to hub | Conversion | hub3 | 87.7564 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 197077.8458 | 197077.8458
Solution 3 | stage0 | pv to hub | Conversion | hub4 | 236.1856 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 194182.194 | 194182.194
Solution 3 | stage0 | pv to hub | Conversion | hub5 | 114.7826 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 107941.5296 | 107941.5296
Solution 3 | stage0 | pv to hub | Conversion | hub6 | 72.5934 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 55518.2903 | 55518.2903
Solution 3 | stage0 | pv to hub | Conversion | hub7 | 85.116 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 155979.3132 | 155979.3132
Solution 3 | stage0 | pv to hub | Conversion | hub8 | 86.4032 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 173515.6061 | 173515.6061
Solution 3 | stage0 | pv to hub | Conversion | hub9 | 485.2683 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 573061.7664 | 573061.7664
Solution 3 | stage0 | pv to electricity | Conversion | plant | 421.0057 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 544411.2343 | 544411.2343
Solution 3 | stage0 | Pump DHW gas | Conversion | hub1 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 3 | stage0 | Pump DHW gas | Conversion | hub10 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 3 | stage0 | Pump DHW gas | Conversion | hub11 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 3 | stage0 | Pump DHW gas | Conversion | hub12 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 3 | stage0 | Pump DHW gas | Conversion | hub13 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 3 | stage0 | Pump DHW gas | Conversion | hub14 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 3 | stage0 | Pump DHW gas | Conversion | hub2 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 3 | stage0 | Pump DHW gas | Conversion | hub3 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 3 | stage0 | Pump DHW gas | Conversion | hub4 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 3 | stage0 | Pump DHW gas | Conversion | hub5 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 3 | stage0 | Pump DHW gas | Conversion | hub6 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 3 | stage0 | Pump DHW gas | Conversion | hub7 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 3 | stage0 | Pump DHW gas | Conversion | hub8 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 3 | stage0 | Pump DHW gas | Conversion | hub9 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 3 | stage0 | HEX pump ETS | Conversion | hub1 | 1506.007 | 1009648.2876 | 61400.2096 | 759776.9816 |  |  | 249871.306 | 0 | 0 | 0 |  |  | 20 |  | 381518.746 | 381518.746
Solution 3 | stage0 | HEX pump ETS | Conversion | hub10 | 106.6678 | 479677.6208 | 29170.8577 | 360965.3177 |  |  | 118712.3031 | 0 | 0 | 0 |  |  | 20 |  | 41913.1391 | 41913.1391
Solution 3 | stage0 | HEX pump ETS | Conversion | hub11 | 167.9563 | 502889.3564 | 30582.4437 | 378432.5314 |  |  | 124456.825 | 0 | 0 | 0 |  |  | 20 |  | 249084.7232 | 249084.7232
Solution 3 | stage0 | HEX pump ETS | Conversion | hub12 | 1922.0431 | 1167213.3499 | 70982.2868 | 878347.2886 |  |  | 288866.0613 | 0 | 0 | 0 |  |  | 20 |  | 5446519.6739 | 5446519.6739
Solution 3 | stage0 | HEX pump ETS | Conversion | hub13 | 104.7669 | 478957.692 | 29127.0763 | 360423.5594 |  |  | 118534.1326 | 0 | 0 | 0 |  |  | 20 |  | 58263.5745 | 58263.5745
Solution 3 | stage0 | HEX pump ETS | Conversion | hub14 | 107.4477 | 479972.9898 | 29188.8201 | 361187.5877 |  |  | 118785.4021 | 0 | 0 | 0 |  |  | 20 |  | 107968.6727 | 107968.6727
Solution 3 | stage0 | HEX pump ETS | Conversion | hub2 | 202.6796 | 516040.1028 | 31382.1861 | 388328.6849 |  |  | 127711.418 | 0 | 0 | 0 |  |  | 20 |  | 68571.8024 | 68571.8024
Solution 3 | stage0 | HEX pump ETS | Conversion | hub3 | 40.274 | 454532.3358 | 27641.6858 | 342043.0762 |  |  | 112489.2596 | 0 | 0 | 0 |  |  | 20 |  | 35623.5905 | 35623.5905
Solution 3 | stage0 | HEX pump ETS | Conversion | hub4 | 189.4114 | 511015.0322 | 31076.5942 | 384547.2364 |  |  | 126467.7958 | 0 | 0 | 0 |  |  | 20 |  | 285271.622 | 285271.622
Solution 3 | stage0 | HEX pump ETS | Conversion | hub5 | 94.0818 | 474910.9353 | 28880.979 | 357378.3082 |  |  | 117532.627 | 0 | 0 | 0 |  |  | 20 |  | 139014.8559 | 139014.8559
Solution 3 | stage0 | HEX pump ETS | Conversion | hub6 | 83.8601 | 471039.6701 | 28645.5539 | 354465.1173 |  |  | 116574.5527 | 0 | 0 | 0 |  |  | 20 |  | 52614.8718 | 52614.8718
Solution 3 | stage0 | HEX pump ETS | Conversion | hub7 | 71.1854 | 466239.3966 | 28353.6327 | 350852.8324 |  |  | 115386.5642 | 0 | 0 | 0 |  |  | 20 |  | 117060.9762 | 117060.9762
Solution 3 | stage0 | HEX pump ETS | Conversion | hub8 | 68.4318 | 465196.5302 | 28290.2124 | 350068.0583 |  |  | 115128.4719 | 0 | 0 | 0 |  |  | 20 |  | 106252.7555 | 106252.7555
Solution 3 | stage0 | HEX pump ETS | Conversion | hub9 | 460.6506 | 613741.2817 | 37323.7332 | 461850.4327 |  |  | 151890.849 | 0 | 0 | 0 |  |  | 20 |  | 481296.4324 | 481296.4324
Solution 3 | stage0 | Main HP | Conversion | plant | 1353.2326 | 2932988.7198 | 178365.2035 | 2207122.3652 |  |  | 725866.3545 | 0 | 0 | 0 |  |  | 20 |  | 6307071.9076 | 6307071.9076
Solution 3 | stage0 | Pump cooling | Conversion | hub1 | 2746.524 | 171158.67 | 10408.7516 | 128799.7209 |  |  | 42358.9491 | 0 | 0 | 0 |  |  | 20 |  | 2915759.2445 | 2915759.2445
Solution 3 | stage0 | Pump cooling | Conversion | hub10 | 43.5653 | 63401.8789 | 3855.6879 | 47710.9591 |  |  | 15690.9198 | 0 | 0 | 0 |  |  | 20 |  | 40007.4138 | 40007.4138
Solution 3 | stage0 | Pump cooling | Conversion | hub11 | 266.7618 | 72299.8815 | 4396.8062 | 54406.8527 |  |  | 17893.0287 | 0 | 0 | 0 |  |  | 20 |  | 591625.2592 | 591625.2592
Solution 3 | stage0 | Pump cooling | Conversion | hub12 | 4679.9342 | 248236.4561 | 15096.1187 | 186802.0256 |  |  | 61434.4304 | 0 | 0 | 0 |  |  | 20 |  | 9316324.8382 | 9316324.8382
Solution 3 | stage0 | Pump cooling | Conversion | hub13 | 151.9881 | 67724.2879 | 4118.5485 | 50963.6432 |  |  | 16760.6448 | 0 | 0 | 0 |  |  | 20 |  | 69307.0831 | 69307.0831
Solution 3 | stage0 | Pump cooling | Conversion | hub14 | 103.6616 | 65797.6909 | 4001.3855 | 49513.8471 |  |  | 16283.8437 | 0 | 0 | 0 |  |  | 20 |  | 51168.1813 | 51168.1813
Solution 3 | stage0 | Pump cooling | Conversion | hub2 | 326.6423 | 74687.0943 | 4541.9809 | 56203.2698 |  |  | 18483.8245 | 0 | 0 | 0 |  |  | 20 |  | 228166.8433 | 228166.8433
Solution 3 | stage0 | Pump cooling | Conversion | hub3 | 100.4378 | 65669.1709 | 3993.5697 | 49417.1337 |  |  | 16252.0372 | 0 | 0 | 0 |  |  | 20 |  | 131510.3058 | 131510.3058
Solution 3 | stage0 | Pump cooling | Conversion | hub4 | 748.031 | 91486.2748 | 5563.5973 | 68844.9301 |  |  | 22641.3448 | 0 | 0 | 0 |  |  | 20 |  | 811707.9698 | 811707.9698
Solution 3 | stage0 | Pump cooling | Conversion | hub5 | 380.9923 | 76853.8252 | 4673.7473 | 57833.7705 |  |  | 19020.0547 | 0 | 0 | 0 |  |  | 20 |  | 422265.8725 | 422265.8725
Solution 3 | stage0 | Pump cooling | Conversion | hub6 | 127.8045 | 66760.1774 | 4059.9176 | 50238.1341 |  |  | 16522.0433 | 0 | 0 | 0 |  |  | 20 |  | 33799.1385 | 33799.1385
Solution 3 | stage0 | Pump cooling | Conversion | hub7 | 264.3832 | 72205.0571 | 4391.0396 | 54335.4958 |  |  | 17869.5612 | 0 | 0 | 0 |  |  | 20 |  | 292396.6081 | 292396.6081
Solution 3 | stage0 | Pump cooling | Conversion | hub8 | 267.1967 | 72317.22 | 4397.8606 | 54419.9003 |  |  | 17897.3197 | 0 | 0 | 0 |  |  | 20 |  | 309788.5739 | 309788.5739
Solution 3 | stage0 | Pump cooling | Conversion | hub9 | 1086.2268 | 104968.8674 | 6383.5204 | 78990.8032 |  |  | 25978.0642 | 0 | 0 | 0 |  |  | 20 |  | 1693852.2016 | 1693852.2016
Solution 3 | stage0 | Pump DHW | Conversion | hub1 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 3 | stage0 | Pump DHW | Conversion | hub10 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 3 | stage0 | Pump DHW | Conversion | hub11 | 34.8297 | 8790.9289 | 534.6068 | 6615.3189 |  |  | 2175.61 | 0 | 0 | 0 |  |  | 20 |  | 157809.6407 | 157809.6407
Solution 3 | stage0 | Pump DHW | Conversion | hub12 | 554.1475 | 11551.3616 | 702.4783 | 8692.59 |  |  | 2858.7716 | 0 | 0 | 0 |  |  | 20 |  | 3432869.3219 | 3432869.3219
Solution 3 | stage0 | Pump DHW | Conversion | hub13 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 3 | stage0 | Pump DHW | Conversion | hub14 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 3 | stage0 | Pump DHW | Conversion | hub2 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 3 | stage0 | Pump DHW | Conversion | hub3 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 3 | stage0 | Pump DHW | Conversion | hub4 | 94.6748 | 9109.0353 | 553.952 | 6854.6992 |  |  | 2254.3361 | 0 | 0 | 0 |  |  | 20 |  | 355179.8886 | 355179.8886
Solution 3 | stage0 | Pump DHW | Conversion | hub5 | 55.1879 | 8899.1428 | 541.1877 | 6696.7517 |  |  | 2202.3911 | 0 | 0 | 0 |  |  | 20 |  | 207042.1928 | 207042.1928
Solution 3 | stage0 | Pump DHW | Conversion | hub6 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 3 | stage0 | Pump DHW | Conversion | hub7 | 43.6957 | 8838.056 | 537.4728 | 6650.7829 |  |  | 2187.2732 | 0 | 0 | 0 |  |  | 20 |  | 163928.5463 | 163928.5463
Solution 3 | stage0 | Pump DHW | Conversion | hub8 | 43.6957 | 8838.056 | 537.4728 | 6650.7829 |  |  | 2187.2732 | 0 | 0 | 0 |  |  | 20 |  | 163928.5463 | 163928.5463
Solution 3 | stage0 | Pump DHW | Conversion | hub9 | 71.4402 | 8985.5316 | 546.4413 | 6761.7607 |  |  | 2223.7709 | 0 | 0 | 0 |  |  | 20 |  | 268013.7936 | 268013.7936
Solution 3 | stage0 | Pump SH | Conversion | hub1 | 2304.5377 | 203386.154 | 12368.6165 | 153051.434 |  |  | 50334.7201 | 0 | 0 | 0 |  |  | 20 |  | 769002.1132 | 769002.1132
Solution 3 | stage0 | Pump SH | Conversion | hub10 | 135.9123 | 93876.5701 | 5708.9594 | 70643.6666 |  |  | 23232.9034 | 0 | 0 | 0 |  |  | 20 |  | 51886.8029 | 51886.8029
Solution 3 | stage0 | Pump SH | Conversion | hub11 | 218.5355 | 98048.8117 | 5962.6879 | 73783.3473 |  |  | 24265.4645 | 0 | 0 | 0 |  |  | 20 |  | 358030.5729 | 358030.5729
Solution 3 | stage0 | Pump SH | Conversion | hub12 | 2153.8699 | 195777.846 | 11905.929 | 147326.0568 |  |  | 48451.7893 | 0 | 0 | 0 |  |  | 20 |  | 7345736.8521 | 7345736.8521
Solution 3 | stage0 | Pump SH | Conversion | hub13 | 140.401 | 94103.2358 | 5722.7437 | 70814.2363 |  |  | 23288.9995 | 0 | 0 | 0 |  |  | 20 |  | 72255.5737 | 72255.5737
Solution 3 | stage0 | Pump SH | Conversion | hub14 | 142.1925 | 94193.7038 | 5728.2454 | 70882.315 |  |  | 23311.3888 | 0 | 0 | 0 |  |  | 20 |  | 133678.2323 | 133678.2323
Solution 3 | stage0 | Pump SH | Conversion | hub2 | 279.8181 | 101143.4144 | 6150.8814 | 76112.0868 |  |  | 25031.3276 | 0 | 0 | 0 |  |  | 20 |  | 85065.6119 | 85065.6119
Solution 3 | stage0 | Pump SH | Conversion | hub3 | 58.7399 | 89979.5802 | 5471.9699 | 67711.1175 |  |  | 22268.4627 | 0 | 0 | 0 |  |  | 20 |  | 44423.8362 | 44423.8362
Solution 3 | stage0 | Pump SH | Conversion | hub4 | 273.5294 | 100825.8515 | 6131.5693 | 75873.1155 |  |  | 24952.736 | 0 | 0 | 0 |  |  | 20 |  | 263452.5885 | 263452.5885
Solution 3 | stage0 | Pump SH | Conversion | hub5 | 136.167 | 93889.4307 | 5709.7415 | 70653.3444 |  |  | 23236.0862 | 0 | 0 | 0 |  |  | 20 |  | 116315.6148 | 116315.6148
Solution 3 | stage0 | Pump SH | Conversion | hub6 | 115.1239 | 92826.813 | 5645.12 | 69853.7071 |  |  | 22973.1059 | 0 | 0 | 0 |  |  | 20 |  | 65178.3221 | 65178.3221
Solution 3 | stage0 | Pump SH | Conversion | hub7 | 104.0534 | 92267.7852 | 5611.1236 | 69433.0295 |  |  | 22834.7557 | 0 | 0 | 0 |  |  | 20 |  | 100816.5425 | 100816.5425
Solution 3 | stage0 | Pump SH | Conversion | hub8 | 100.9653 | 92111.8452 | 5601.6404 | 69315.682 |  |  | 22796.1631 | 0 | 0 | 0 |  |  | 20 |  | 97713.9952 | 97713.9952
Solution 3 | stage0 | Pump SH | Conversion | hub9 | 674.3585 | 121066.6146 | 7362.4802 | 91104.6234 |  |  | 29961.9912 | 0 | 0 | 0 |  |  | 20 |  | 577006.576 | 577006.576
Solution 3 | stage0 | HEX SC ets | Conversion | hub1 | 8.8973 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 768922.7721 | 768.9228
Solution 3 | stage0 | HEX SC ets | Conversion | hub10 | 0.30656 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 83919.5038 | 83.9195
Solution 3 | stage0 | HEX SC ets | Conversion | hub11 | 0.59251 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 505235.274 | 505.2353
Solution 3 | stage0 | HEX SC ets | Conversion | hub12 | 4.0488 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 10893244.078 | 10893.2441
Solution 3 | stage0 | HEX SC ets | Conversion | hub13 | 0.46855 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 119604.1349 | 119.6041
Solution 3 | stage0 | HEX SC ets | Conversion | hub14 | 0.4369 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 216159.3488 | 216.1593
Solution 3 | stage0 | HEX SC ets | Conversion | hub2 | 1.1052 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 140131.6702 | 140.1317
Solution 3 | stage0 | HEX SC ets | Conversion | hub3 | 0.29564 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 79124.8274 | 79.1248
Solution 3 | stage0 | HEX SC ets | Conversion | hub4 | 1.3202 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 605210.4918 | 605.2105
Solution 3 | stage0 | HEX SC ets | Conversion | hub5 | 0.65858 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 290323.6344 | 290.3236
Solution 3 | stage0 | HEX SC ets | Conversion | hub6 | 0.44146 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 106324.6963 | 106.3247
Solution 3 | stage0 | HEX SC ets | Conversion | hub7 | 0.516 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 246471.3605 | 246.4714
Solution 3 | stage0 | HEX SC ets | Conversion | hub8 | 0.51751 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 226364.4196 | 226.3644
Solution 3 | stage0 | HEX SC ets | Conversion | hub9 | 3.0999 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 972687.3231 | 972.6873
Solution 3 | stage0 | ETS HP | Conversion | hub1 | 2942.74 | 8160047.4971 | 496240.7534 | 6140570.2691 |  |  | 2019477.228 | 0 | 0 | 0 |  |  | 20 |  | 191368.5694 | 2870477.2387
Solution 3 | stage0 | ETS HP | Conversion | hub10 | 46.7128 | 155257.2966 | 9441.734 | 116833.6753 |  |  | 38423.6213 | 0 | 0 | 0 |  |  | 20 |  | 2867.2999 | 42933.4945
Solution 3 | stage0 | ETS HP | Conversion | hub11 | 304.4511 | 867661.1768 | 52765.4816 | 652929.3399 |  |  | 214731.8369 | 0 | 0 | 0 |  |  | 20 |  | 66875.4776 | 656593.6823
Solution 3 | stage0 | ETS HP | Conversion | hub12 | 5359.4493 | 14839974.4708 | 902470.2509 | 11167325.4429 |  |  | 3672649.0279 | 0 | 0 | 0 |  |  | 20 |  | 1221719.6438 | 10803773.4881
Solution 3 | stage0 | ETS HP | Conversion | hub13 | 162.8801 | 476350.5423 | 28968.5265 | 358461.6362 |  |  | 117888.906 | 0 | 0 | 0 |  |  | 20 |  | 5057.3296 | 75811.094
Solution 3 | stage0 | ETS HP | Conversion | hub14 | 111.1017 | 333231.9035 | 20264.9863 | 250762.5011 |  |  | 82469.4024 | 0 | 0 | 0 |  |  | 20 |  | 3666.3527 | 54948.0522
Solution 3 | stage0 | ETS HP | Conversion | hub2 | 350.0096 | 993587.5886 | 60423.5029 | 747691.0408 |  |  | 245896.5478 | 0 | 0 | 0 |  |  | 20 |  | 16405.7526 | 245945.6541
Solution 3 | stage0 | ETS HP | Conversion | hub3 | 107.6476 | 323684.7024 | 19684.3879 | 243578.0749 |  |  | 80106.6275 | 0 | 0 | 0 |  |  | 20 |  | 9666.8329 | 144871.8282
Solution 3 | stage0 | ETS HP | Conversion | hub4 | 843.4468 | 2357477.0194 | 143366.3435 | 1774040.3228 |  |  | 583436.6967 | 0 | 0 | 0 |  |  | 20 |  | 125915.8553 | 1105740.2043
Solution 3 | stage0 | ETS HP | Conversion | hub5 | 431.0509 | 1217590.5623 | 74045.8996 | 916256.9715 |  |  | 301333.5908 | 0 | 0 | 0 |  |  | 20 |  | 69360.0698 | 588073.3063
Solution 3 | stage0 | ETS HP | Conversion | hub6 | 136.9691 | 404730.9017 | 24613.0881 | 304566.676 |  |  | 100164.2257 | 0 | 0 | 0 |  |  | 20 |  | 2454.9005 | 36777.0078
Solution 3 | stage0 | ETS HP | Conversion | hub7 | 301.8022 | 860339.3813 | 52320.2179 | 647419.5681 |  |  | 212919.8132 | 0 | 0 | 0 |  |  | 20 |  | 52064.9693 | 422150.8779
Solution 3 | stage0 | ETS HP | Conversion | hub8 | 305.5068 | 870579.012 | 52942.9253 | 655125.059 |  |  | 215453.953 | 0 | 0 | 0 |  |  | 20 |  | 52916.3277 | 433035.2371
Solution 3 | stage0 | ETS HP | Conversion | hub9 | 1205.2119 | 3357417.1441 | 204176.1661 | 2526511.7518 |  |  | 830905.3924 | 0 | 0 | 0 |  |  | 20 |  | 170989.3636 | 1946932.2719
Solution 3 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub1 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -2.8399e-11 | -2.5559e-11
Solution 3 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub10 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -1.7615e-12 | -1.5854e-12
Solution 3 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub11 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -2.2719e-11 | -2.0447e-11
Solution 3 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub12 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -2.9902e-10 | -2.6912e-10
Solution 3 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub13 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -9.4298e-12 | -8.4869e-12
Solution 3 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub14 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -5.6267e-12 | -5.064e-12
Solution 3 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub2 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -3.0027e-12 | -2.7024e-12
Solution 3 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub3 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -3.5654e-12 | -3.2089e-12
Solution 3 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub4 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -2.2433e-11 | -2.019e-11
Solution 3 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub5 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -4.2456e-12 | -3.8211e-12
Solution 3 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub6 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -7.0586e-12 | -6.3528e-12
Solution 3 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub7 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -3.6544e-12 | -3.289e-12
Solution 3 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub8 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -9.137e-12 | -8.2233e-12
Solution 3 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub9 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -3.7457e-11 | -3.3712e-11
Solution 3 | stage0 | rooftop to pv | Conversion | plant | 6584.7276 | 23698681.007 | 1441198.8805 | 23046546.6 |  |  | 3789711.2159 | 0 | 3137576.809 | 0 |  |  | 25 |  | 8694079.8505 | 8694079.8505
Solution 3 | stage0 | battery | Storage | plant | 4551.1495 | 4463648.1905 | 271449.9078 | 3445220.1647 |  |  | 0 | 2581878.8801 | 1563450.8542 | 0 |  |  | 15 |  | 1688829.0412 | 1688829.0412
Solution 3 | stage0 | Generic Hot Water Storage hub1 | Storage | hub1 | 0.27028 | 14948.9498 | 909.0974 | 13813.2437 |  |  | 1135.706 | 0 | 0 | 0 |  |  | 20 |  | 25.651 | 0
Solution 3 | stage0 | Generic Hot Water Storage hub2 | Storage | hub2 | 0.74387 | 14974.0639 | 910.6247 | 13836.4499 |  |  | 1137.614 | 0 | 0 | 0 |  |  | 20 |  | 70.3174 | 0
Solution 3 | stage0 | Generic Hot Water Storage hub3 | Storage | hub3 | 0.68698 | 14971.0466 | 910.4412 | 13833.6618 |  |  | 1137.3848 | 0 | 0 | 0 |  |  | 20 |  | 65.3325 | 0
Solution 3 | stage0 | Generic Hot Water Storage hub4 | Storage | hub4 | 467.9774 | 39750.8572 | 2417.3873 | 36730.8933 |  |  | 3019.9639 | 0 | 0 | 0 |  |  | 20 |  | 175382.6556 | 139063.7318
Solution 3 | stage0 | Generic Hot Water Storage hub5 | Storage | hub5 | 247.8556 | 28078.081 | 1707.5254 | 25944.9247 |  |  | 2133.1563 | 0 | 0 | 0 |  |  | 20 |  | 95834.4436 | 76712.7658
Solution 3 | stage0 | Generic Hot Water Storage hub6 | Storage | hub6 | 0.26712 | 14948.7824 | 909.0872 | 13813.0891 |  |  | 1135.6933 | 0 | 0 | 0 |  |  | 20 |  | 23.2499 | 0
Solution 3 | stage0 | Generic Hot Water Storage hub7 | Storage | hub7 | 203.082 | 25703.7957 | 1563.1369 | 23751.0193 |  |  | 1952.7764 | 0 | 0 | 0 |  |  | 20 |  | 78698.5602 | 63215.2757
Solution 3 | stage0 | Generic Hot Water Storage hub8 | Storage | hub8 | 213.6464 | 26264.011 | 1597.2055 | 24268.6738 |  |  | 1995.3372 | 0 | 0 | 0 |  |  | 20 |  | 81227.2773 | 64800.9842
Solution 3 | stage0 | Generic Hot Water Storage hub9 | Storage | hub9 | 501.8655 | 41547.9009 | 2526.6718 | 38391.4114 |  |  | 3156.4895 | 0 | 0 | 0 |  |  | 20 |  | 159206.6523 | 118266.3552
Solution 3 | stage0 | Generic Hot Water Storage hub10 | Storage | hub10 | 0.42749 | 14957.2862 | 909.6044 | 13820.9468 |  |  | 1136.3394 | 0 | 0 | 0 |  |  | 20 |  | 38.0022 | 0
Solution 3 | stage0 | Generic Hot Water Storage hub11 | Storage | hub11 | 203.0812 | 25703.7517 | 1563.1342 | 23750.9786 |  |  | 1952.773 | 0 | 0 | 0 |  |  | 20 |  | 62216.3375 | 46756.7371
Solution 3 | stage0 | Generic Hot Water Storage hub12 | Storage | hub12 | 4289.7861 | 242416.4532 | 14742.1842 | 223999.5185 |  |  | 18416.9347 | 0 | 0 | 0 |  |  | 20 |  | 1456935.6908 | 1128794.4283
Solution 3 | stage0 | Generic Hot Water Storage hub13 | Storage | hub13 | 0.26628 | 14948.7376 | 909.0845 | 13813.0477 |  |  | 1135.6899 | 0 | 0 | 0 |  |  | 20 |  | 24.4247 | 0
Solution 3 | stage0 | Generic Hot Water Storage hub14 | Storage | hub14 | 0.27028 | 14948.9498 | 909.0974 | 13813.2437 |  |  | 1135.706 | 0 | 0 | 0 |  |  | 20 |  | 23.6191 | 0
Solution 3 | stage0 | Generic Borehole | Storage | plant | 9500000 | 10571597.206 | 642895.4444 | 14250000 |  |  | 1171615.5519 | 0 | 4850018.3459 | 0 |  |  | 40 |  | 11203658.9173 | 9741435.4834
Solution 3 | stage0 | Anergy | Network | hub1_to_hub2_Anergy | 7902.4821 | 478628.6295 | 29107.0649 | 580800 |  |  | 95505.1667 | 0 | 197676.5372 | 0 |  |  | 40 | 528 | 6934219.2999 | 11497559.8394
Solution 3 | stage0 | Anergy | Network | hub3_to_hub4_Anergy | 7557.5757 | 452340.3146 | 27508.3814 | 548900 |  |  | 90259.6177 | 0 | 186819.3032 | 0 |  |  | 40 | 499 | 6844741.8836 | 11114545.7759
Solution 3 | stage0 | Anergy | Network | hub5_to_hub6_Anergy | 6447.1015 | 317272.7657 | 19294.4559 | 385000 |  |  | 63308.3491 | 0 | 131035.5834 | 0 |  |  | 40 | 350 | 6441990.6817 | 10045812.103
Solution 3 | stage0 | Anergy | Network | hub7_to_hub8_Anergy | 6228.776 | 180392.2297 | 10970.2763 | 218900 |  |  | 35995.3185 | 0 | 74503.0888 | 0 |  |  | 40 | 199 | 6278994.1798 | 9768484.8098
Solution 3 | stage0 | Anergy | Network | hub9_to_hub10_Anergy | 4945.9411 | 758735.1569 | 46141.313 | 920700 |  |  | 151397.3949 | 0 | 313362.238 | 0 |  |  | 40 | 837 | 5744773.4361 | 7880271.2982
Solution 3 | stage0 | Anergy | Network | hub11_to_hub12_Anergy | 4654.5394 | 591940.3315 | 35997.9419 | 718300 |  |  | 118115.2914 | 0 | 244474.9598 | 0 |  |  | 40 | 653 | 5471870.5565 | 7355049.8913
Solution 3 | stage0 | Anergy | Network | hub13_to_hub14_Anergy | 113.8479 | 383446.7997 | 23318.7281 | 465300 |  |  | 76512.6619 | 0 | 158365.8622 | 0 |  |  | 40 | 423 | 105269.4559 | 56218.904
Solution 3 | stage0 | pv_loop | Network | hub1_to_hub2_pv_loop | 3157.0146 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 528 | 6841308.8479 | 0
Solution 3 | stage0 | pv_loop | Network | hub3_to_hub4_pv_loop | 2995.6954 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 499 | 6479556.5127 | 0
Solution 3 | stage0 | pv_loop | Network | hub5_to_hub6_pv_loop | 2644.7272 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 350 | 6177432.7892 | 0
Solution 3 | stage0 | pv_loop | Network | hub7_to_hub8_pv_loop | 2557.5667 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 199 | 5965935.1857 | 0
Solution 3 | stage0 | pv_loop | Network | hub9_to_hub10_pv_loop | 2013.8056 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 837 | 5219357.8132 | 0
Solution 3 | stage0 | pv_loop | Network | hub11_to_hub12_pv_loop | 1887.682 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 653 | 4863645.3052 | 0
Solution 3 | stage0 | pv_loop | Network | hub13_to_hub14_pv_loop | 58.1681 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 423 | 78165.1388 | 0
Solution 3 | stage0 | Anergy | Network | plant_to_hub1_Anergy | 10658.0156 | 94275.3361 | 5733.2097 | 114400 |  |  | 18811.6237 | 0 | 38936.2876 | 0 |  |  | 40 | 104 | 7085296.787 | 14217691.3673
Solution 3 | stage0 | Anergy | Network | hub2_to_hub3_Anergy | 7667.1604 | 109685.7276 | 6670.369 | 133100 |  |  | 21886.6007 | 0 | 45300.8731 | 0 |  |  | 40 | 121 | 6878483.098 | 11258033.6536
Solution 3 | stage0 | Anergy | Network | hub4_to_hub5_Anergy | 6813.0744 | 119657.1574 | 7276.7662 | 145200 |  |  | 23876.2917 | 0 | 49419.1343 | 0 |  |  | 40 | 132 | 6573409.2081 | 10406575.734
Solution 3 | stage0 | Anergy | Network | hub6_to_hub7_Anergy | 6436.5766 | 145945.4722 | 8875.4497 | 177100 |  |  | 29121.8406 | 0 | 60276.3684 | 0 |  |  | 40 | 161 | 6391039.4788 | 10009025.7524
Solution 3 | stage0 | Anergy | Network | hub8_to_hub9_Anergy | 6063.1708 | 1264558.5949 | 76902.1884 | 1534500 |  |  | 252328.9915 | 0 | 522270.3966 | 0 |  |  | 40 | 1395 | 6178067.5852 | 9519102.4022
Solution 3 | stage0 | Anergy | Network | hub10_to_hub11_Anergy | 4899.4487 | 144132.485 | 8765.1957 | 174900 |  |  | 28760.0786 | 0 | 59527.5936 | 0 |  |  | 40 | 159 | 5703979.1847 | 7836394.7887
Solution 3 | stage0 | Anergy | Network | hub12_to_hub13_Anergy | 228.6265 | 286451.9828 | 17420.1373 | 347600 |  |  | 57158.3952 | 0 | 118306.4124 | 0 |  |  | 40 | 316 | 162072.071 | 132366.5097
Solution 3 | stage0 | pv_loop | Network | plant_to_hub1_pv_loop | 4162.1831 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 104 | 8160581.2497 | 0
Solution 3 | stage0 | pv_loop | Network | hub2_to_hub3_pv_loop | 3083.4519 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 121 | 6676634.3585 | 0
Solution 3 | stage0 | pv_loop | Network | hub4_to_hub5_pv_loop | 2759.5098 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 132 | 6285374.3188 | 0
Solution 3 | stage0 | pv_loop | Network | hub6_to_hub7_pv_loop | 2642.6827 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 161 | 6121914.4989 | 0
Solution 3 | stage0 | pv_loop | Network | hub8_to_hub9_pv_loop | 2478.1452 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 1395 | 5792419.5796 | 0
Solution 3 | stage0 | pv_loop | Network | hub10_to_hub11_pv_loop | 1998.7284 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 159 | 5166084.5832 | 0
Solution 3 | stage0 | pv_loop | Network | hub12_to_hub13_pv_loop | 62.151 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 316 | 138069.0707 | 0
Solution 4 | stage0 | Gas | Import | hub10 | 0 | -8.3397e-12 | -5.0717e-13 |  | -8.3397e-12 |  | 0 |  |  |  | -3.6226e-11 |  |  |  | -9.0566e-12
Solution 4 | stage0 | Gas | Import | hub8 | 0 | -1.5968e-11 | -9.7104e-13 |  | -1.5968e-11 |  | 0 |  |  |  | -6.936e-11 |  |  |  | -1.734e-11
Solution 4 | stage0 | Gas | Import | hub11 | 0 | -5.9086e-11 | -3.5932e-12 |  | -5.9086e-11 |  | 0 |  |  |  | -2.5666e-10 |  |  |  | -6.4165e-11
Solution 4 | stage0 | Gas | Import | hub7 | 0 | -1.5164e-11 | -9.2219e-13 |  | -1.5164e-11 |  | 0 |  |  |  | -6.5871e-11 |  |  |  | -1.6468e-11
Solution 4 | stage0 | Gas | Import | hub14 | 0 | -2.1809e-11 | -1.3263e-12 |  | -2.1809e-11 |  | 0 |  |  |  | -9.4736e-11 |  |  |  | -2.3684e-11
Solution 4 | stage0 | Gas | Import | hub2 | 0 | -1.3552e-11 | -8.2417e-13 |  | -1.3552e-11 |  | 0 |  |  |  | -5.8869e-11 |  |  |  | -1.4717e-11
Solution 4 | stage0 | Gas | Import | hub3 | 0 | -7.6874e-12 | -4.675e-13 |  | -7.6874e-12 |  | 0 |  |  |  | -3.3393e-11 |  |  |  | -8.3481e-12
Solution 4 | stage0 | Gas | Import | hub4 | 0 | -4.2837e-11 | -2.6051e-12 |  | -4.2837e-11 |  | 0 |  |  |  | -1.8608e-10 |  |  |  | -4.6519e-11
Solution 4 | stage0 | Gas | Import | hub6 | 0 | -9.7264e-12 | -5.9149e-13 |  | -9.7264e-12 |  | 0 |  |  |  | -4.225e-11 |  |  |  | -1.0562e-11
Solution 4 | stage0 | Gas | Import | hub1 | 0 | -1.2806e-10 | -7.7877e-12 |  | -1.2806e-10 |  | 0 |  |  |  | -5.5626e-10 |  |  |  | -1.3907e-10
Solution 4 | stage0 | Gas | Import | hub13 | 0 | -1.1369e-11 | -6.9137e-13 |  | -1.1369e-11 |  | 0 |  |  |  | -4.9383e-11 |  |  |  | -1.2346e-11
Solution 4 | stage0 | Gas | Import | hub5 | 0 | -1.8954e-11 | -1.1526e-12 |  | -1.8954e-11 |  | 0 |  |  |  | -8.2331e-11 |  |  |  | -2.0583e-11
Solution 4 | stage0 | Gas | Import | hub9 | 0 | -1.0008e-10 | -6.0863e-12 |  | -1.0008e-10 |  | 0 |  |  |  | -4.3473e-10 |  |  |  | -1.0868e-10
Solution 4 | stage0 | Gas | Import | hub12 | 0 | -1.1966e-09 | -7.2769e-11 |  | -1.1966e-09 |  | 0 |  |  |  | -5.1978e-09 |  |  |  | -1.2994e-09
Solution 4 | stage0 | Heat ambient in | Import | plant | 0 | 0 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0
Solution 4 | stage0 | Electricity | Import | hub10 | 34.5973 | 72243.7939 | 4393.3953 |  | 72243.7939 |  | 0 |  |  |  | 149970.3477 |  |  |  | 31893.9532
Solution 4 | stage0 | Electricity | Import | plant | 0 | 0 | 0 |  | 0 |  | 0 |  |  |  | 0 |  |  |  | 0
Solution 4 | stage0 | Electricity | Import | hub8 | 134.7451 | 353265.542 | 21483.3013 |  | 353265.542 |  | 0 |  |  |  | 808733.0137 |  |  |  | 157370.0444
Solution 4 | stage0 | Electricity | Import | hub11 | 139.1664 | 443343.2634 | 26961.2395 |  | 443343.2634 |  | 0 |  |  |  | 1018561.3406 |  |  |  | 200714.9558
Solution 4 | stage0 | Electricity | Import | hub7 | 135.2954 | 326032.7804 | 19827.1827 |  | 326032.7804 |  | 0 |  |  |  | 770164.8531 |  |  |  | 149128.4981
Solution 4 | stage0 | Electricity | Import | hub14 | 52.3005 | 136899.8513 | 8325.3542 |  | 136899.8513 |  | 0 |  |  |  | 292694.6764 |  |  |  | 61849.9202
Solution 4 | stage0 | Electricity | Import | hub2 | 93.1875 | 238714.9707 | 14517.0842 |  | 238714.9707 |  | 0 |  |  |  | 486392.3539 |  |  |  | 106393.6689
Solution 4 | stage0 | Electricity | Import | hub3 | 82.6327 | 387700.8608 | 23577.4323 |  | 387700.8608 |  | 0 |  |  |  | 851265.7169 |  |  |  | 181052.0591
Solution 4 | stage0 | Electricity | Import | hub4 | 368.1621 | 804615.0769 | 48931.4299 |  | 804615.0769 |  | 0 |  |  |  | 1914616.7032 |  |  |  | 374075.0189
Solution 4 | stage0 | Electricity | Import | hub6 | 22.0814 | 27270.1013 | 1658.3893 |  | 27270.1013 |  | 0 |  |  |  | 51573.2995 |  |  |  | 11722.4123
Solution 4 | stage0 | Electricity | Import | hub1 | 1261.6655 | 2302871.3417 | 140045.5831 |  | 2302871.3417 |  | 0 |  |  |  | 4365587.7564 |  |  |  | 1020324.977
Solution 4 | stage0 | Electricity | Import | hub13 | 42.4625 | 109780.7856 | 6676.1498 |  | 109780.7856 |  | 0 |  |  |  | 213641.3423 |  |  |  | 47770.36
Solution 4 | stage0 | Electricity | Import | hub5 | 221.4554 | 528562.6983 | 32143.7285 |  | 528562.6983 |  | 0 |  |  |  | 1229048.4381 |  |  |  | 237553.7214
Solution 4 | stage0 | Electricity | Import | hub9 | 616.3826 | 2401012.9849 | 146013.9163 |  | 2401012.9849 |  | 0 |  |  |  | 5239134.2794 |  |  |  | 1075168.0672
Solution 4 | stage0 | Electricity | Import | hub12 | 2049.4292 | 10728898.4705 | 652461.4792 |  | 10728898.4705 |  | 0 |  |  |  | 24064600.3359 |  |  |  | 4925855.1478
Solution 4 | stage0 | Slack | Export | hub10 | 0.30656 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 83.9859
Solution 4 | stage0 | Slack | Export | hub8 | 0.59486 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 255.0426
Solution 4 | stage0 | Slack | Export | hub11 | 0.35302 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 519.7912
Solution 4 | stage0 | Slack | Export | hub7 | 0.56142 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 276.3667
Solution 4 | stage0 | Slack | Export | hub14 | 0.4369 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 216.2379
Solution 4 | stage0 | Slack | Export | hub2 | 0.45201 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 137.3641
Solution 4 | stage0 | Slack | Export | hub3 | 0.10017 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 71.8037
Solution 4 | stage0 | Slack | Export | hub4 | 0.54157 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 635.9818
Solution 4 | stage0 | Slack | Export | hub6 | 0.18597 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 105.3954
Solution 4 | stage0 | Slack | Export | hub1 | 8.8973 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 768.9728
Solution 4 | stage0 | Slack | Export | hub13 | 0.37588 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 116.9569
Solution 4 | stage0 | Slack | Export | hub5 | 0.51606 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 330.001
Solution 4 | stage0 | Slack | Export | hub9 | 1.6167 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 989.3864
Solution 4 | stage0 | Slack | Export | hub12 | 9.3523 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 11327.9464
Solution 4 | stage0 | Heat ambient out | Export | plant | 4024.8833 | 0 | 0 |  |  | 0 | 0 |  |  |  |  | 0 |  |  |  | 6746273.8336
Solution 4 | stage0 | export_electricity | Export | plant | 4397.0824 | -1062449.611 | -64611.241 |  |  | 1062449.611 | 0 |  |  |  |  | 0 |  |  |  | 2153708.0335
Solution 4 | stage0 | parking to pv | Conversion | plant | 5043.6508 | 20745471.77 | 1261603.9974 | 20174603.04 |  |  | 3317456.6561 | 0 | 2746587.926 | 0 |  |  | 25 |  | 6659334.3125 | 6659334.3125
Solution 4 | stage0 | cooling tower plant | Conversion | plant | 4024.8833 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 6746273.8336 | 6746273.8336
Solution 4 | stage0 | pv to hub | Conversion | hub1 | 1584.2629 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 2193624.3508 | 2193624.3508
Solution 4 | stage0 | pv to hub | Conversion | hub10 | 35.0766 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 46988.1648 | 46988.1648
Solution 4 | stage0 | pv to hub | Conversion | hub11 | 191.9448 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 363842.508 | 363842.508
Solution 4 | stage0 | pv to hub | Conversion | hub12 | 2281.6613 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 5855528.6572 | 5855528.6572
Solution 4 | stage0 | pv to hub | Conversion | hub13 | 66.6593 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 57290.6716 | 57290.6716
Solution 4 | stage0 | pv to hub | Conversion | hub14 | 60.4908 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 71551.0898 | 71551.0898
Solution 4 | stage0 | pv to hub | Conversion | hub2 | 143.7961 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 224963.5681 | 224963.5681
Solution 4 | stage0 | pv to hub | Conversion | hub3 | 90.3808 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 262356.8504 | 262356.8504
Solution 4 | stage0 | pv to hub | Conversion | hub4 | 308.8689 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 573718.9812 | 573718.9812
Solution 4 | stage0 | pv to hub | Conversion | hub5 | 155.8117 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 303602.0522 | 303602.0522
Solution 4 | stage0 | pv to hub | Conversion | hub6 | 73.2644 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 54802.3883 | 54802.3883
Solution 4 | stage0 | pv to hub | Conversion | hub7 | 115.5563 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 202809.2374 | 202809.2374
Solution 4 | stage0 | pv to hub | Conversion | hub8 | 104.0852 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 201105.3735 | 201105.3735
Solution 4 | stage0 | pv to hub | Conversion | hub9 | 774.5333 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 1399484.2301 | 1399484.2301
Solution 4 | stage0 | pv to electricity | Conversion | plant | 1126.9673 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 1388038.006 | 1388038.006
Solution 4 | stage0 | Pump DHW gas | Conversion | hub1 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 4 | stage0 | Pump DHW gas | Conversion | hub10 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 4 | stage0 | Pump DHW gas | Conversion | hub11 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 4 | stage0 | Pump DHW gas | Conversion | hub12 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 4 | stage0 | Pump DHW gas | Conversion | hub13 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 4 | stage0 | Pump DHW gas | Conversion | hub14 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 4 | stage0 | Pump DHW gas | Conversion | hub2 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 4 | stage0 | Pump DHW gas | Conversion | hub3 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 4 | stage0 | Pump DHW gas | Conversion | hub4 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 4 | stage0 | Pump DHW gas | Conversion | hub5 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 4 | stage0 | Pump DHW gas | Conversion | hub6 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 4 | stage0 | Pump DHW gas | Conversion | hub7 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 4 | stage0 | Pump DHW gas | Conversion | hub8 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 4 | stage0 | Pump DHW gas | Conversion | hub9 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 4 | stage0 | HEX pump ETS | Conversion | hub1 | 1506.007 | 1009648.2876 | 61400.2096 | 759776.9816 |  |  | 249871.306 | 0 | 0 | 0 |  |  | 20 |  | 381543.7573 | 381543.7573
Solution 4 | stage0 | HEX pump ETS | Conversion | hub10 | 106.6678 | 479677.6208 | 29170.8577 | 360965.3177 |  |  | 118712.3031 | 0 | 0 | 0 |  |  | 20 |  | 41946.3442 | 41946.3442
Solution 4 | stage0 | HEX pump ETS | Conversion | hub11 | 176.5094 | 506128.6862 | 30779.4386 | 380870.1805 |  |  | 125258.5057 | 0 | 0 | 0 |  |  | 20 |  | 259895.5967 | 259895.5967
Solution 4 | stage0 | HEX pump ETS | Conversion | hub12 | 2748.1068 | 1480067.8376 | 90008.0519 | 1113775.4484 |  |  | 366292.3892 | 0 | 0 | 0 |  |  | 20 |  | 5601521.4937 | 5601521.4937
Solution 4 | stage0 | HEX pump ETS | Conversion | hub13 | 108.0765 | 480211.1456 | 29203.3031 | 361366.8039 |  |  | 118844.3417 | 0 | 0 | 0 |  |  | 20 |  | 58398.5824 | 58398.5824
Solution 4 | stage0 | HEX pump ETS | Conversion | hub14 | 107.4477 | 479972.9898 | 29188.8201 | 361187.5877 |  |  | 118785.4021 | 0 | 0 | 0 |  |  | 20 |  | 108007.9577 | 108007.9577
Solution 4 | stage0 | HEX pump ETS | Conversion | hub2 | 226.0069 | 524874.837 | 31919.4569 | 394976.968 |  |  | 129897.869 | 0 | 0 | 0 |  |  | 20 |  | 68682.0551 | 68682.0551
Solution 4 | stage0 | HEX pump ETS | Conversion | hub3 | 47.2552 | 457176.3366 | 27802.4766 | 344032.7304 |  |  | 113143.6062 | 0 | 0 | 0 |  |  | 20 |  | 35899.031 | 35899.031
Solution 4 | stage0 | HEX pump ETS | Conversion | hub4 | 220.7909 | 522899.398 | 31799.3236 | 393490.4176 |  |  | 129408.9804 | 0 | 0 | 0 |  |  | 20 |  | 317479.2486 | 317479.2486
Solution 4 | stage0 | HEX pump ETS | Conversion | hub5 | 109.7622 | 480849.5572 | 29242.1272 | 361847.2191 |  |  | 119002.3381 | 0 | 0 | 0 |  |  | 20 |  | 160768.5398 | 160768.5398
Solution 4 | stage0 | HEX pump ETS | Conversion | hub6 | 92.9847 | 474495.4248 | 28855.7104 | 357065.6298 |  |  | 117429.7951 | 0 | 0 | 0 |  |  | 20 |  | 52697.6839 | 52697.6839
Solution 4 | stage0 | HEX pump ETS | Conversion | hub7 | 83.6398 | 470956.2374 | 28640.4801 | 354402.3329 |  |  | 116553.9045 | 0 | 0 | 0 |  |  | 20 |  | 132571.4193 | 132571.4193
Solution 4 | stage0 | HEX pump ETS | Conversion | hub8 | 82.0974 | 470372.1048 | 28604.957 | 353962.7634 |  |  | 116409.3413 | 0 | 0 | 0 |  |  | 20 |  | 121343.976 | 121343.976
Solution 4 | stage0 | HEX pump ETS | Conversion | hub9 | 513.6232 | 633803.5228 | 38543.7876 | 476947.5998 |  |  | 156855.9229 | 0 | 0 | 0 |  |  | 20 |  | 494398.4901 | 494398.4901
Solution 4 | stage0 | Main HP | Conversion | plant | 3622.395 | 7851158.4802 | 477456.1423 | 5908126.1915 |  |  | 1943032.2887 | 0 | 0 | 0 |  |  | 20 |  | 6071646.4503 | 6071646.4503
Solution 4 | stage0 | Pump cooling | Conversion | hub1 | 2746.524 | 171158.67 | 10408.7516 | 128799.7209 |  |  | 42358.9491 | 0 | 0 | 0 |  |  | 20 |  | 2915759.2445 | 2915759.2445
Solution 4 | stage0 | Pump cooling | Conversion | hub10 | 43.5653 | 63401.8789 | 3855.6879 | 47710.9591 |  |  | 15690.9198 | 0 | 0 | 0 |  |  | 20 |  | 40007.4138 | 40007.4138
Solution 4 | stage0 | Pump cooling | Conversion | hub11 | 266.7618 | 72299.8815 | 4396.8062 | 54406.8527 |  |  | 17893.0287 | 0 | 0 | 0 |  |  | 20 |  | 591625.2592 | 591625.2592
Solution 4 | stage0 | Pump cooling | Conversion | hub12 | 4679.9342 | 248236.4561 | 15096.1187 | 186802.0256 |  |  | 61434.4304 | 0 | 0 | 0 |  |  | 20 |  | 9316324.8382 | 9316324.8382
Solution 4 | stage0 | Pump cooling | Conversion | hub13 | 151.9881 | 67724.2879 | 4118.5485 | 50963.6432 |  |  | 16760.6448 | 0 | 0 | 0 |  |  | 20 |  | 69307.0831 | 69307.0831
Solution 4 | stage0 | Pump cooling | Conversion | hub14 | 103.6616 | 65797.6909 | 4001.3855 | 49513.8471 |  |  | 16283.8437 | 0 | 0 | 0 |  |  | 20 |  | 51168.1813 | 51168.1813
Solution 4 | stage0 | Pump cooling | Conversion | hub2 | 326.6423 | 74687.0943 | 4541.9809 | 56203.2698 |  |  | 18483.8245 | 0 | 0 | 0 |  |  | 20 |  | 228166.8433 | 228166.8433
Solution 4 | stage0 | Pump cooling | Conversion | hub3 | 100.4378 | 65669.1709 | 3993.5697 | 49417.1337 |  |  | 16252.0372 | 0 | 0 | 0 |  |  | 20 |  | 131510.3058 | 131510.3058
Solution 4 | stage0 | Pump cooling | Conversion | hub4 | 748.031 | 91486.2748 | 5563.5973 | 68844.9301 |  |  | 22641.3448 | 0 | 0 | 0 |  |  | 20 |  | 811707.9698 | 811707.9698
Solution 4 | stage0 | Pump cooling | Conversion | hub5 | 380.9923 | 76853.8252 | 4673.7473 | 57833.7705 |  |  | 19020.0547 | 0 | 0 | 0 |  |  | 20 |  | 422265.8725 | 422265.8725
Solution 4 | stage0 | Pump cooling | Conversion | hub6 | 127.8045 | 66760.1774 | 4059.9176 | 50238.1341 |  |  | 16522.0433 | 0 | 0 | 0 |  |  | 20 |  | 33799.1385 | 33799.1385
Solution 4 | stage0 | Pump cooling | Conversion | hub7 | 264.3832 | 72205.0571 | 4391.0396 | 54335.4958 |  |  | 17869.5612 | 0 | 0 | 0 |  |  | 20 |  | 292396.6081 | 292396.6081
Solution 4 | stage0 | Pump cooling | Conversion | hub8 | 267.1967 | 72317.22 | 4397.8606 | 54419.9003 |  |  | 17897.3197 | 0 | 0 | 0 |  |  | 20 |  | 309788.5739 | 309788.5739
Solution 4 | stage0 | Pump cooling | Conversion | hub9 | 1086.2268 | 104968.8674 | 6383.5204 | 78990.8032 |  |  | 25978.0642 | 0 | 0 | 0 |  |  | 20 |  | 1693852.2016 | 1693852.2016
Solution 4 | stage0 | Pump DHW | Conversion | hub1 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 4 | stage0 | Pump DHW | Conversion | hub10 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 4 | stage0 | Pump DHW | Conversion | hub11 | 34.8297 | 8790.9289 | 534.6068 | 6615.3189 |  |  | 2175.61 | 0 | 0 | 0 |  |  | 20 |  | 157809.6407 | 157809.6407
Solution 4 | stage0 | Pump DHW | Conversion | hub12 | 554.1475 | 11551.3616 | 702.4783 | 8692.59 |  |  | 2858.7716 | 0 | 0 | 0 |  |  | 20 |  | 3432869.3219 | 3432869.3219
Solution 4 | stage0 | Pump DHW | Conversion | hub13 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 4 | stage0 | Pump DHW | Conversion | hub14 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 4 | stage0 | Pump DHW | Conversion | hub2 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 4 | stage0 | Pump DHW | Conversion | hub3 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 4 | stage0 | Pump DHW | Conversion | hub4 | 94.6748 | 9109.0353 | 553.952 | 6854.6992 |  |  | 2254.3361 | 0 | 0 | 0 |  |  | 20 |  | 355179.8886 | 355179.8886
Solution 4 | stage0 | Pump DHW | Conversion | hub5 | 55.1879 | 8899.1428 | 541.1877 | 6696.7517 |  |  | 2202.3911 | 0 | 0 | 0 |  |  | 20 |  | 207042.1928 | 207042.1928
Solution 4 | stage0 | Pump DHW | Conversion | hub6 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | 0 | 0
Solution 4 | stage0 | Pump DHW | Conversion | hub7 | 43.6957 | 8838.056 | 537.4728 | 6650.7829 |  |  | 2187.2732 | 0 | 0 | 0 |  |  | 20 |  | 163928.5463 | 163928.5463
Solution 4 | stage0 | Pump DHW | Conversion | hub8 | 43.6957 | 8838.056 | 537.4728 | 6650.7829 |  |  | 2187.2732 | 0 | 0 | 0 |  |  | 20 |  | 163928.5463 | 163928.5463
Solution 4 | stage0 | Pump DHW | Conversion | hub9 | 71.4402 | 8985.5316 | 546.4413 | 6761.7607 |  |  | 2223.7709 | 0 | 0 | 0 |  |  | 20 |  | 268013.7936 | 268013.7936
Solution 4 | stage0 | Pump SH | Conversion | hub1 | 2304.5377 | 203386.154 | 12368.6165 | 153051.434 |  |  | 50334.7201 | 0 | 0 | 0 |  |  | 20 |  | 769002.1132 | 769002.1132
Solution 4 | stage0 | Pump SH | Conversion | hub10 | 135.9123 | 93876.5701 | 5708.9594 | 70643.6666 |  |  | 23232.9034 | 0 | 0 | 0 |  |  | 20 |  | 51886.8029 | 51886.8029
Solution 4 | stage0 | Pump SH | Conversion | hub11 | 218.5355 | 98048.8117 | 5962.6879 | 73783.3473 |  |  | 24265.4645 | 0 | 0 | 0 |  |  | 20 |  | 358030.5729 | 358030.5729
Solution 4 | stage0 | Pump SH | Conversion | hub12 | 2153.8699 | 195777.846 | 11905.929 | 147326.0568 |  |  | 48451.7893 | 0 | 0 | 0 |  |  | 20 |  | 7345736.8521 | 7345736.8521
Solution 4 | stage0 | Pump SH | Conversion | hub13 | 140.401 | 94103.2358 | 5722.7437 | 70814.2363 |  |  | 23288.9995 | 0 | 0 | 0 |  |  | 20 |  | 72255.5737 | 72255.5737
Solution 4 | stage0 | Pump SH | Conversion | hub14 | 142.1925 | 94193.7038 | 5728.2454 | 70882.315 |  |  | 23311.3888 | 0 | 0 | 0 |  |  | 20 |  | 133678.2323 | 133678.2323
Solution 4 | stage0 | Pump SH | Conversion | hub2 | 279.8181 | 101143.4144 | 6150.8814 | 76112.0868 |  |  | 25031.3276 | 0 | 0 | 0 |  |  | 20 |  | 85065.6119 | 85065.6119
Solution 4 | stage0 | Pump SH | Conversion | hub3 | 58.7399 | 89979.5802 | 5471.9699 | 67711.1175 |  |  | 22268.4627 | 0 | 0 | 0 |  |  | 20 |  | 44423.8362 | 44423.8362
Solution 4 | stage0 | Pump SH | Conversion | hub4 | 273.5294 | 100825.8515 | 6131.5693 | 75873.1155 |  |  | 24952.736 | 0 | 0 | 0 |  |  | 20 |  | 263452.5885 | 263452.5885
Solution 4 | stage0 | Pump SH | Conversion | hub5 | 136.167 | 93889.4307 | 5709.7415 | 70653.3444 |  |  | 23236.0862 | 0 | 0 | 0 |  |  | 20 |  | 116315.6148 | 116315.6148
Solution 4 | stage0 | Pump SH | Conversion | hub6 | 115.1239 | 92826.813 | 5645.12 | 69853.7071 |  |  | 22973.1059 | 0 | 0 | 0 |  |  | 20 |  | 65178.3221 | 65178.3221
Solution 4 | stage0 | Pump SH | Conversion | hub7 | 104.0534 | 92267.7852 | 5611.1236 | 69433.0295 |  |  | 22834.7557 | 0 | 0 | 0 |  |  | 20 |  | 100816.5425 | 100816.5425
Solution 4 | stage0 | Pump SH | Conversion | hub8 | 100.9653 | 92111.8452 | 5601.6404 | 69315.682 |  |  | 22796.1631 | 0 | 0 | 0 |  |  | 20 |  | 97713.9952 | 97713.9952
Solution 4 | stage0 | Pump SH | Conversion | hub9 | 674.3585 | 121066.6146 | 7362.4802 | 91104.6234 |  |  | 29961.9912 | 0 | 0 | 0 |  |  | 20 |  | 577006.576 | 577006.576
Solution 4 | stage0 | HEX SC ets | Conversion | hub1 | 8.8973 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 768972.7946 | 768.9728
Solution 4 | stage0 | HEX SC ets | Conversion | hub10 | 0.30656 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 83985.914 | 83.9859
Solution 4 | stage0 | HEX SC ets | Conversion | hub11 | 0.35302 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 519791.1934 | 519.7912
Solution 4 | stage0 | HEX SC ets | Conversion | hub12 | 9.3523 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 11327946.4268 | 11327.9464
Solution 4 | stage0 | HEX SC ets | Conversion | hub13 | 0.37588 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 116956.8928 | 116.9569
Solution 4 | stage0 | HEX SC ets | Conversion | hub14 | 0.4369 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 216237.9187 | 216.2379
Solution 4 | stage0 | HEX SC ets | Conversion | hub2 | 0.45201 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 137364.1103 | 137.3641
Solution 4 | stage0 | HEX SC ets | Conversion | hub3 | 0.1 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 71803.7199 | 71.8037
Solution 4 | stage0 | HEX SC ets | Conversion | hub4 | 0.54157 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 635981.7679 | 635.9818
Solution 4 | stage0 | HEX SC ets | Conversion | hub5 | 0.51606 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 330000.9897 | 330.001
Solution 4 | stage0 | HEX SC ets | Conversion | hub6 | 0.18597 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 105395.3678 | 105.3954
Solution 4 | stage0 | HEX SC ets | Conversion | hub7 | 0.56142 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 276366.6527 | 276.3667
Solution 4 | stage0 | HEX SC ets | Conversion | hub8 | 0.59486 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 255042.6337 | 255.0426
Solution 4 | stage0 | HEX SC ets | Conversion | hub9 | 1.6167 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 1 |  | 989386.4026 | 989.3864
Solution 4 | stage0 | ETS HP | Conversion | hub1 | 2942.74 | 8160047.4971 | 496240.7534 | 6140570.2691 |  |  | 2019477.228 | 0 | 0 | 0 |  |  | 20 |  | 191389.9564 | 2870548.5832
Solution 4 | stage0 | ETS HP | Conversion | hub10 | 46.7179 | 155271.2922 | 9442.5851 | 116844.2072 |  |  | 38427.085 | 0 | 0 | 0 |  |  | 20 |  | 2886.9354 | 43008.3071
Solution 4 | stage0 | ETS HP | Conversion | hub11 | 370.1519 | 1049262.0001 | 63809.2567 | 789586.9534 |  |  | 259675.0468 | 0 | 0 | 0 |  |  | 20 |  | 72853.1692 | 676795.672
Solution 4 | stage0 | ETS HP | Conversion | hub12 | 6233.1649 | 17254976.0313 | 1049334.861 | 12984653.9312 |  |  | 4270322.1001 | 0 | 0 | 0 |  |  | 20 |  | 1296297.9434 | 11170861.6003
Solution 4 | stage0 | ETS HP | Conversion | hub13 | 162.8801 | 476350.5423 | 28968.5265 | 358461.6362 |  |  | 117888.906 | 0 | 0 | 0 |  |  | 20 |  | 4982.5007 | 74437.7364
Solution 4 | stage0 | ETS HP | Conversion | hub14 | 111.1017 | 333231.9035 | 20264.9863 | 250762.5011 |  |  | 82469.4024 | 0 | 0 | 0 |  |  | 20 |  | 3688.5696 | 55034.2588
Solution 4 | stage0 | ETS HP | Conversion | hub2 | 350.0096 | 993587.5886 | 60423.5029 | 747691.0408 |  |  | 245896.5478 | 0 | 0 | 0 |  |  | 20 |  | 16319.5489 | 244491.7547
Solution 4 | stage0 | ETS HP | Conversion | hub3 | 107.6476 | 323684.7024 | 19684.3879 | 243578.0749 |  |  | 80106.6275 | 0 | 0 | 0 |  |  | 20 |  | 9418.4642 | 140979.5777
Solution 4 | stage0 | ETS HP | Conversion | hub4 | 886.9535 | 2477732.1466 | 150679.4743 | 1864534.2885 |  |  | 613197.8581 | 0 | 0 | 0 |  |  | 20 |  | 133267.5269 | 1136435.4926
Solution 4 | stage0 | ETS HP | Conversion | hub5 | 458.0442 | 1292201.5066 | 78583.2496 | 972402.9371 |  |  | 319798.5695 | 0 | 0 | 0 |  |  | 20 |  | 74657.9272 | 618149.0526
Solution 4 | stage0 | ETS HP | Conversion | hub6 | 136.9691 | 404730.9017 | 24613.0881 | 304566.676 |  |  | 100164.2257 | 0 | 0 | 0 |  |  | 20 |  | 2440.7172 | 36322.3509
Solution 4 | stage0 | ETS HP | Conversion | hub7 | 322.6838 | 918057.2766 | 55830.243 | 690853.2358 |  |  | 227204.0407 | 0 | 0 | 0 |  |  | 20 |  | 56128.3348 | 444974.5688
Solution 4 | stage0 | ETS HP | Conversion | hub8 | 325.6982 | 926389.3805 | 56336.9471 | 697123.2814 |  |  | 229266.0991 | 0 | 0 | 0 |  |  | 20 |  | 56805.8605 | 454910.6361
Solution 4 | stage0 | ETS HP | Conversion | hub9 | 1228.2967 | 3421225.0166 | 208056.5438 | 2574528.2277 |  |  | 846696.7889 | 0 | 0 | 0 |  |  | 20 |  | 174849.3029 | 1963295.352
Solution 4 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub1 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -2.2397e-11 | -2.0157e-11
Solution 4 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub10 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -1.7924e-12 | -1.6131e-12
Solution 4 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub11 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -1.3728e-11 | -1.2355e-11
Solution 4 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub12 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -2.8422e-10 | -2.558e-10
Solution 4 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub13 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -3.3274e-12 | -2.9947e-12
Solution 4 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub14 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -5.6267e-12 | -5.064e-12
Solution 4 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub2 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -3.0644e-12 | -2.7579e-12
Solution 4 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub3 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -2.5458e-12 | -2.2912e-12
Solution 4 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub4 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -9.8335e-12 | -8.8501e-12
Solution 4 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub5 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -4.7082e-12 | -4.2374e-12
Solution 4 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub6 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -1.9788e-12 | -1.7809e-12
Solution 4 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub7 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -3.6853e-12 | -3.3167e-12
Solution 4 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub8 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -3.4722e-12 | -3.125e-12
Solution 4 | stage0 | Gas Boiler (Linearized cost) | Conversion | hub9 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 |  | -2.3529e-11 | -2.1176e-11
Solution 4 | stage0 | rooftop to pv | Conversion | plant | 6584.7276 | 23698681.007 | 1441198.8805 | 23046546.6 |  |  | 3789711.2159 | 0 | 3137576.809 | 0 |  |  | 25 |  | 8694079.8505 | 8694079.8505
Solution 4 | stage0 | battery | Storage | plant | 8607 | 8441520.1153 | 513358.0783 | 6515499 |  |  | 0 | 4882773.3663 | 2956752.251 | 0 |  |  | 15 |  | 3167703.0917 | 3167703.0917
Solution 4 | stage0 | Generic Hot Water Storage hub1 | Storage | hub1 | 1.566 | 15017.6623 | 913.2761 | 13876.736 |  |  | 1140.9263 | 0 | 0 | 0 |  |  | 20 |  | 150.3818 | 0
Solution 4 | stage0 | Generic Hot Water Storage hub2 | Storage | hub2 | 1.5659 | 15017.6529 | 913.2755 | 13876.7273 |  |  | 1140.9256 | 0 | 0 | 0 |  |  | 20 |  | 150.7391 | 0
Solution 4 | stage0 | Generic Hot Water Storage hub3 | Storage | hub3 | 1.5465 | 15016.628 | 913.2132 | 13875.7803 |  |  | 1140.8477 | 0 | 0 | 0 |  |  | 20 |  | 148.6924 | 0
Solution 4 | stage0 | Generic Hot Water Storage hub4 | Storage | hub4 | 1139 | 75334.3214 | 4581.341 | 69611 |  |  | 5723.3214 | 0 | 0 | 0 |  |  | 20 |  | 259102.8887 | 182994.0716
Solution 4 | stage0 | Generic Hot Water Storage hub5 | Storage | hub5 | 664 | 50145.6827 | 3049.5327 | 46336 |  |  | 3809.6827 | 0 | 0 | 0 |  |  | 20 |  | 150425.9243 | 106608.1897
Solution 4 | stage0 | Generic Hot Water Storage hub6 | Storage | hub6 | 1.4886 | 15013.5582 | 913.0265 | 13872.9437 |  |  | 1140.6145 | 0 | 0 | 0 |  |  | 20 |  | 144.2034 | 0
Solution 4 | stage0 | Generic Hot Water Storage hub7 | Storage | hub7 | 525 | 42774.6916 | 2601.2772 | 39525 |  |  | 3249.6916 | 0 | 0 | 0 |  |  | 20 |  | 117994.0174 | 83447.3368
Solution 4 | stage0 | Generic Hot Water Storage hub8 | Storage | hub8 | 525 | 42774.6916 | 2601.2772 | 39525 |  |  | 3249.6916 | 0 | 0 | 0 |  |  | 20 |  | 119194.7831 | 84534.6939
Solution 4 | stage0 | Generic Hot Water Storage hub9 | Storage | hub9 | 859 | 60486.2817 | 3678.3803 | 55891 |  |  | 4595.2817 | 0 | 0 | 0 |  |  | 20 |  | 203923.0075 | 142214.7056
Solution 4 | stage0 | Generic Hot Water Storage hub10 | Storage | hub10 | 1.5382 | 15016.1886 | 913.1864 | 13875.3742 |  |  | 1140.8143 | 0 | 0 | 0 |  |  | 20 |  | 147.8622 | 0
Solution 4 | stage0 | Generic Hot Water Storage hub11 | Storage | hub11 | 633 | 48501.7926 | 2949.562 | 44817 |  |  | 3684.7926 | 0 | 0 | 0 |  |  | 20 |  | 126352.0358 | 76160.7433
Solution 4 | stage0 | Generic Hot Water Storage hub12 | Storage | hub12 | 11220 | 609916.7784 | 37091.152 | 563580 |  |  | 46336.7784 | 0 | 0 | 0 |  |  | 20 |  | 2356452.4585 | 1652518.0051
Solution 4 | stage0 | Generic Hot Water Storage hub13 | Storage | hub13 | 1.5574 | 15017.2047 | 913.2482 | 13876.3132 |  |  | 1140.8915 | 0 | 0 | 0 |  |  | 20 |  | 149.8868 | 0
Solution 4 | stage0 | Generic Hot Water Storage hub14 | Storage | hub14 | 1.5299 | 15015.7444 | 913.1594 | 13874.9638 |  |  | 1140.7806 | 0 | 0 | 0 |  |  | 20 |  | 147.1425 | 0
Solution 4 | stage0 | Generic Borehole | Storage | plant | 9500000 | 10571597.206 | 642895.4444 | 14250000 |  |  | 1171615.5519 | 0 | 4850018.3459 | 0 |  |  | 40 |  | 11468186.1182 | 10011333.658
Solution 4 | stage0 | Anergy | Network | hub1_to_hub2_Anergy | 7439.1284 | 478628.6295 | 29107.0649 | 580800 |  |  | 95505.1667 | 0 | 197676.5372 | 0 |  |  | 40 | 528 | 7133144.4518 | 11379257.84
Solution 4 | stage0 | Anergy | Network | hub3_to_hub4_Anergy | 7235.0015 | 452340.3146 | 27508.3814 | 548900 |  |  | 90259.6177 | 0 | 186819.3032 | 0 |  |  | 40 | 499 | 7050429.212 | 11003463.9572
Solution 4 | stage0 | Anergy | Network | hub5_to_hub6_Anergy | 6244.1562 | 317272.7657 | 19294.4559 | 385000 |  |  | 63308.3491 | 0 | 131035.5834 | 0 |  |  | 40 | 350 | 6614187.5836 | 9938444.8744
Solution 4 | stage0 | Anergy | Network | hub7_to_hub8_Anergy | 6026.3933 | 180392.2297 | 10970.2763 | 218900 |  |  | 35995.3185 | 0 | 74503.0888 | 0 |  |  | 40 | 199 | 6442602.0641 | 9663326.9026
Solution 4 | stage0 | Anergy | Network | hub9_to_hub10_Anergy | 4827.6466 | 758735.1569 | 46141.313 | 920700 |  |  | 151397.3949 | 0 | 313362.238 | 0 |  |  | 40 | 837 | 5902989.4574 | 7792347.0927
Solution 4 | stage0 | Anergy | Network | hub11_to_hub12_Anergy | 4542.6692 | 591940.3315 | 35997.9419 | 718300 |  |  | 118115.2914 | 0 | 244474.9598 | 0 |  |  | 40 | 653 | 5622419.1938 | 7281345.982
Solution 4 | stage0 | Anergy | Network | hub13_to_hub14_Anergy | 113.8479 | 383446.7997 | 23318.7281 | 465300 |  |  | 76512.6619 | 0 | 158365.8622 | 0 |  |  | 40 | 423 | 105307.7587 | 56180.6304
Solution 4 | stage0 | pv_loop | Network | hub1_to_hub2_pv_loop | 4372.8725 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 528 | 9618043.7727 | 0
Solution 4 | stage0 | pv_loop | Network | hub3_to_hub4_pv_loop | 4138.6957 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 499 | 9130723.3543 | 0
Solution 4 | stage0 | pv_loop | Network | hub5_to_hub6_pv_loop | 3674.0152 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 350 | 8253402.3208 | 0
Solution 4 | stage0 | pv_loop | Network | hub7_to_hub8_pv_loop | 3485.1945 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 199 | 7995790.6951 | 0
Solution 4 | stage0 | pv_loop | Network | hub9_to_hub10_pv_loop | 2612.4803 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 837 | 6395201.0915 | 0
Solution 4 | stage0 | pv_loop | Network | hub11_to_hub12_pv_loop | 2388.2346 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 653 | 5984370.4187 | 0
Solution 4 | stage0 | pv_loop | Network | hub13_to_hub14_pv_loop | 60.4908 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 423 | 71551.0898 | 0
Solution 4 | stage0 | Anergy | Network | plant_to_hub1_Anergy | 9948.7565 | 94275.3361 | 5733.2097 | 114400 |  |  | 18811.6237 | 0 | 38936.2876 | 0 |  |  | 40 | 104 | 7257260.8436 | 14072349.1314
Solution 4 | stage0 | Anergy | Network | hub2_to_hub3_Anergy | 7344.5862 | 109685.7276 | 6670.369 | 133100 |  |  | 21886.6007 | 0 | 45300.8731 | 0 |  |  | 40 | 121 | 7081915.2013 | 11144387.4233
Solution 4 | stage0 | Anergy | Network | hub4_to_hub5_Anergy | 6570.8203 | 119657.1574 | 7276.7662 | 145200 |  |  | 23876.2917 | 0 | 49419.1343 | 0 |  |  | 40 | 132 | 6757658.0041 | 10297532.297
Solution 4 | stage0 | Anergy | Network | hub6_to_hub7_Anergy | 6244.1562 | 145945.4722 | 8875.4497 | 177100 |  |  | 29121.8406 | 0 | 60276.3684 | 0 |  |  | 40 | 161 | 6563426.5063 | 9901958.2467
Solution 4 | stage0 | Anergy | Network | hub8_to_hub9_Anergy | 5805.5387 | 1264558.5949 | 76902.1884 | 1534500 |  |  | 252328.9915 | 0 | 522270.3966 | 0 |  |  | 40 | 1395 | 6333653.5981 | 9416130.1878
Solution 4 | stage0 | Anergy | Network | hub10_to_hub11_Anergy | 4786.0131 | 144132.485 | 8765.1957 | 174900 |  |  | 28760.0786 | 0 | 59527.5936 | 0 |  |  | 40 | 159 | 5862302.7203 | 7748646.4185
Solution 4 | stage0 | Anergy | Network | hub12_to_hub13_Anergy | 228.5606 | 286451.9828 | 17420.1373 | 347600 |  |  | 57158.3952 | 0 | 118306.4124 | 0 |  |  | 40 | 316 | 162219.0072 | 132264.0155
Solution 4 | stage0 | pv_loop | Network | plant_to_hub1_pv_loop | 5957.1355 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 104 | 11811668.1236 | 0
Solution 4 | stage0 | pv_loop | Network | hub2_to_hub3_pv_loop | 4229.0765 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 121 | 9393080.2046 | 0
Solution 4 | stage0 | pv_loop | Network | hub4_to_hub5_pv_loop | 3829.8268 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 132 | 8557004.373 | 0
Solution 4 | stage0 | pv_loop | Network | hub6_to_hub7_pv_loop | 3600.7508 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 161 | 8198599.9324 | 0
Solution 4 | stage0 | pv_loop | Network | hub8_to_hub9_pv_loop | 3381.1092 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 1395 | 7794685.3216 | 0
Solution 4 | stage0 | pv_loop | Network | hub10_to_hub11_pv_loop | 2579.6258 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 159 | 6348212.9267 | 0
Solution 4 | stage0 | pv_loop | Network | hub12_to_hub13_pv_loop | 124.5007 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  |  | 20 | 316 | 128841.7615 | 0

## Capacity Planning
Solution | Install Stage | Phaseout Stage | Name | Type | Hub or Link | Capacity (kW or KWh) | Investment (USD) | Replacement Years | Replacement cost (USD) | Salvage revenue (USD) | Embodied CO2 emissions (kg-CO2)
Solution 1 | stage0 | stage0 | ETS HP | Conversion | hub1 | 2942.74 | 6140570.2691 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | ETS HP | Conversion | hub10 | 46.7128 | 116833.6753 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | ETS HP | Conversion | hub11 | 308.2411 | 660812.4722 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | ETS HP | Conversion | hub12 | 5306.7548 | 11057720.9709 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | ETS HP | Conversion | hub13 | 162.8801 | 358461.6362 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | ETS HP | Conversion | hub14 | 111.1017 | 250762.5011 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | ETS HP | Conversion | hub2 | 350.0096 | 747691.0408 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | ETS HP | Conversion | hub3 | 107.6476 | 243578.0749 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | ETS HP | Conversion | hub4 | 904.2163 | 1900440.8527 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | ETS HP | Conversion | hub5 | 454.5568 | 965149.118 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | ETS HP | Conversion | hub6 | 136.9691 | 304566.676 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | ETS HP | Conversion | hub7 | 317.2977 | 679650.121 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | ETS HP | Conversion | hub8 | 318.2995 | 681733.857 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | ETS HP | Conversion | hub9 | 1231.827 | 2581871.1168 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX SC ets | Conversion | hub1 | 8.8973 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX SC ets | Conversion | hub10 | 0.30656 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX SC ets | Conversion | hub11 | 0.61341 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX SC ets | Conversion | hub12 | 3.8336 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX SC ets | Conversion | hub13 | 0.49702 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX SC ets | Conversion | hub14 | 0.4369 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX SC ets | Conversion | hub2 | 1.1052 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX SC ets | Conversion | hub3 | 0.29564 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX SC ets | Conversion | hub4 | 1.4197 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX SC ets | Conversion | hub5 | 0.79459 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX SC ets | Conversion | hub6 | 0.44146 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX SC ets | Conversion | hub7 | 0.58171 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX SC ets | Conversion | hub8 | 0.58905 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX SC ets | Conversion | hub9 | 3.0105 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX pump ETS | Conversion | hub1 | 1506.007 | 759776.9816 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX pump ETS | Conversion | hub10 | 106.6678 | 360965.3177 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX pump ETS | Conversion | hub11 | 167.2098 | 378219.7879 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX pump ETS | Conversion | hub12 | 1916.7844 | 876848.5611 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX pump ETS | Conversion | hub13 | 103.75 | 360133.736 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX pump ETS | Conversion | hub14 | 107.4477 | 361187.5877 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX pump ETS | Conversion | hub2 | 202.6796 | 388328.6849 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX pump ETS | Conversion | hub3 | 40.274 | 342043.0762 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX pump ETS | Conversion | hub4 | 185.8581 | 383534.5715 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX pump ETS | Conversion | hub5 | 89.2241 | 355993.8569 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX pump ETS | Conversion | hub6 | 83.8601 | 354465.1173 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX pump ETS | Conversion | hub7 | 68.8388 | 350184.0706 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX pump ETS | Conversion | hub8 | 65.8765 | 349339.7976 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | HEX pump ETS | Conversion | hub9 | 463.8445 | 462760.6684 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Main HP | Conversion | plant | 1158.4775 | 1889476.7348 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump DHW | Conversion | hub11 | 34.8297 | 6615.3189 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump DHW | Conversion | hub12 | 554.1475 | 8692.59 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump DHW | Conversion | hub4 | 94.6748 | 6854.6992 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump DHW | Conversion | hub5 | 55.1879 | 6696.7517 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump DHW | Conversion | hub7 | 43.6957 | 6650.7829 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump DHW | Conversion | hub8 | 43.6957 | 6650.7829 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump DHW | Conversion | hub9 | 71.4402 | 6761.7607 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump SH | Conversion | hub1 | 2304.5377 | 153051.434 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump SH | Conversion | hub10 | 135.9123 | 70643.6666 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump SH | Conversion | hub11 | 218.5355 | 73783.3473 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump SH | Conversion | hub12 | 2153.8699 | 147326.0568 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump SH | Conversion | hub13 | 140.401 | 70814.2363 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump SH | Conversion | hub14 | 142.1925 | 70882.315 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump SH | Conversion | hub2 | 279.8181 | 76112.0868 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump SH | Conversion | hub3 | 58.7399 | 67711.1175 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump SH | Conversion | hub4 | 273.5294 | 75873.1155 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump SH | Conversion | hub5 | 136.167 | 70653.3444 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump SH | Conversion | hub6 | 115.1239 | 69853.7071 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump SH | Conversion | hub7 | 104.0534 | 69433.0295 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump SH | Conversion | hub8 | 100.9653 | 69315.682 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump SH | Conversion | hub9 | 674.3585 | 91104.6234 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump cooling | Conversion | hub1 | 2746.524 | 128799.7209 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump cooling | Conversion | hub10 | 43.5653 | 47710.9591 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump cooling | Conversion | hub11 | 266.7618 | 54406.8527 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump cooling | Conversion | hub12 | 4679.9342 | 186802.0256 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump cooling | Conversion | hub13 | 151.9881 | 50963.6432 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump cooling | Conversion | hub14 | 103.6616 | 49513.8471 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump cooling | Conversion | hub2 | 326.6423 | 56203.2698 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump cooling | Conversion | hub3 | 100.4378 | 49417.1337 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump cooling | Conversion | hub4 | 748.031 | 68844.9301 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump cooling | Conversion | hub5 | 380.9923 | 57833.7705 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump cooling | Conversion | hub6 | 127.8045 | 50238.1341 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump cooling | Conversion | hub7 | 264.3832 | 54335.4958 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump cooling | Conversion | hub8 | 267.1967 | 54419.9003 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Pump cooling | Conversion | hub9 | 1086.2268 | 78990.8032 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | cooling tower plant | Conversion | plant | 1287.1972 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | pv to hub | Conversion | hub1 | 37.6957 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | pv to hub | Conversion | hub10 | 0.66081 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | pv to hub | Conversion | hub11 | 2.9197 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | pv to hub | Conversion | hub12 | 5.003 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | pv to hub | Conversion | hub13 | 0.1 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | pv to hub | Conversion | hub14 | 3.3543 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | pv to hub | Conversion | hub2 | 18.0835 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | pv to hub | Conversion | hub3 | 3.0233 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | pv to hub | Conversion | hub4 | 9.2811 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | pv to hub | Conversion | hub5 | 1.5814 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | pv to hub | Conversion | hub6 | 18.2194 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | pv to hub | Conversion | hub7 | 0.1 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | pv to hub | Conversion | hub8 | 0.79303 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | pv to hub | Conversion | hub9 | 5.003 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | rooftop to pv | Conversion | plant | 76.734 | 268568.8417 |  | 0 | 36563.1947 | 0
Solution 1 | stage0 | stage0 | Generic Hot Water Storage hub1 | Storage | hub1 | 0.27367 | 13813.4099 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Generic Hot Water Storage hub2 | Storage | hub2 | 0.19151 | 13809.384 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Generic Hot Water Storage hub3 | Storage | hub3 | 0.6601 | 13832.3451 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Generic Hot Water Storage hub4 | Storage | hub4 | 494.4199 | 38026.5738 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Generic Hot Water Storage hub5 | Storage | hub5 | 270.1843 | 27039.0325 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Generic Hot Water Storage hub6 | Storage | hub6 | 0.26712 | 13813.0891 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Generic Hot Water Storage hub7 | Storage | hub7 | 245.2537 | 25817.4321 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Generic Hot Water Storage hub8 | Storage | hub8 | 250.1121 | 26055.4927 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Generic Hot Water Storage hub9 | Storage | hub9 | 640.8508 | 45201.6892 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Generic Hot Water Storage hub10 | Storage | hub10 | 0.29546 | 13814.4778 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Generic Hot Water Storage hub11 | Storage | hub11 | 180.8518 | 22661.7363 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Generic Hot Water Storage hub12 | Storage | hub12 | 3112.2186 | 166298.7111 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Generic Hot Water Storage hub13 | Storage | hub13 | 0.26628 | 13813.0477 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Generic Hot Water Storage hub14 | Storage | hub14 | 0.16049 | 13807.8641 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Generic Borehole | Storage | plant | 9500000 | 14250000 |  | 0 | 4850018.3459 | 0
Solution 1 | stage0 | stage0 | Anergy | Network | hub1_to_hub2_Anergy | 7735.8223 | 580800 |  | 0 | 197676.5372 | 0
Solution 1 | stage0 | stage0 | Anergy | Network | hub3_to_hub4_Anergy | 7405.6881 | 548900 |  | 0 | 186819.3032 | 0
Solution 1 | stage0 | stage0 | Anergy | Network | hub5_to_hub6_Anergy | 6515.1791 | 385000 |  | 0 | 131035.5834 | 0
Solution 1 | stage0 | stage0 | Anergy | Network | hub7_to_hub8_Anergy | 6244.3897 | 218900 |  | 0 | 74503.0888 | 0
Solution 1 | stage0 | stage0 | Anergy | Network | hub9_to_hub10_Anergy | 5034.4096 | 920700 |  | 0 | 313362.238 | 0
Solution 1 | stage0 | stage0 | Anergy | Network | hub11_to_hub12_Anergy | 4749.8369 | 718300 |  | 0 | 244474.9598 | 0
Solution 1 | stage0 | stage0 | Anergy | Network | hub13_to_hub14_Anergy | 113.8479 | 465300 |  | 0 | 158365.8622 | 0
Solution 1 | stage0 | stage0 | pv_loop | Network | hub1_to_hub2_pv_loop | 39.0382 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | pv_loop | Network | hub3_to_hub4_pv_loop | 18.7548 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | pv_loop | Network | hub5_to_hub6_pv_loop | 18.7548 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | pv_loop | Network | hub7_to_hub8_pv_loop | 5.003 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | pv_loop | Network | hub9_to_hub10_pv_loop | 5.003 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | pv_loop | Network | hub11_to_hub12_pv_loop | 5.003 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | pv_loop | Network | hub13_to_hub14_pv_loop | 3.3543 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | Anergy | Network | plant_to_hub1_Anergy | 10491.3558 | 114400 |  | 0 | 38936.2876 | 0
Solution 1 | stage0 | stage0 | Anergy | Network | hub2_to_hub3_Anergy | 7515.2728 | 133100 |  | 0 | 45300.8731 | 0
Solution 1 | stage0 | stage0 | Anergy | Network | hub4_to_hub5_Anergy | 6773.3766 | 145200 |  | 0 | 49419.1343 | 0
Solution 1 | stage0 | stage0 | Anergy | Network | hub6_to_hub7_Anergy | 6440.2743 | 177100 |  | 0 | 60276.3684 | 0
Solution 1 | stage0 | stage0 | Anergy | Network | hub8_to_hub9_Anergy | 6102.4018 | 1534500 |  | 0 | 522270.3966 | 0
Solution 1 | stage0 | stage0 | Anergy | Network | hub10_to_hub11_Anergy | 4987.7493 | 174900 |  | 0 | 59527.5936 | 0
Solution 1 | stage0 | stage0 | Anergy | Network | hub12_to_hub13_Anergy | 228.6848 | 347600 |  | 0 | 118306.4124 | 0
Solution 1 | stage0 | stage0 | pv_loop | Network | plant_to_hub1_pv_loop | 76.734 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | pv_loop | Network | hub2_to_hub3_pv_loop | 20.9548 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | pv_loop | Network | hub4_to_hub5_pv_loop | 18.7548 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | pv_loop | Network | hub6_to_hub7_pv_loop | 5.003 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | pv_loop | Network | hub8_to_hub9_pv_loop | 5.003 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | pv_loop | Network | hub10_to_hub11_pv_loop | 5.003 | 0 |  | 0 | 0 | 0
Solution 1 | stage0 | stage0 | pv_loop | Network | hub12_to_hub13_pv_loop | 3.3543 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | ETS HP | Conversion | hub1 | 2942.74 | 6140570.2691 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | ETS HP | Conversion | hub10 | 46.7128 | 116833.6753 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | ETS HP | Conversion | hub11 | 308.2411 | 660812.4722 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | ETS HP | Conversion | hub12 | 5310.3877 | 11065277.3222 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | ETS HP | Conversion | hub13 | 162.8801 | 358461.6362 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | ETS HP | Conversion | hub14 | 111.1017 | 250762.5011 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | ETS HP | Conversion | hub2 | 350.0096 | 747691.0408 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | ETS HP | Conversion | hub3 | 107.6476 | 243578.0749 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | ETS HP | Conversion | hub4 | 890.3732 | 1871647.1827 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | ETS HP | Conversion | hub5 | 454.7032 | 965453.5747 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | ETS HP | Conversion | hub6 | 136.9691 | 304566.676 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | ETS HP | Conversion | hub7 | 320.1752 | 685635.4281 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | ETS HP | Conversion | hub8 | 325.5675 | 696851.4534 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | ETS HP | Conversion | hub9 | 1231.3486 | 2580876.1877 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX SC ets | Conversion | hub1 | 8.8973 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX SC ets | Conversion | hub10 | 0.30656 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX SC ets | Conversion | hub11 | 0.61341 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX SC ets | Conversion | hub12 | 3.8336 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX SC ets | Conversion | hub13 | 0.47613 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX SC ets | Conversion | hub14 | 0.4369 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX SC ets | Conversion | hub2 | 1.1052 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX SC ets | Conversion | hub3 | 0.29564 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX SC ets | Conversion | hub4 | 1.4166 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX SC ets | Conversion | hub5 | 0.78215 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX SC ets | Conversion | hub6 | 0.44146 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX SC ets | Conversion | hub7 | 0.5632 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX SC ets | Conversion | hub8 | 0.56463 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX SC ets | Conversion | hub9 | 3.0121 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX pump ETS | Conversion | hub1 | 1506.007 | 759776.9816 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX pump ETS | Conversion | hub10 | 106.6678 | 360965.3177 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX pump ETS | Conversion | hub11 | 167.2098 | 378219.7879 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX pump ETS | Conversion | hub12 | 1916.8039 | 876854.1232 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX pump ETS | Conversion | hub13 | 104.4963 | 360346.4403 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX pump ETS | Conversion | hub14 | 107.4477 | 361187.5877 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX pump ETS | Conversion | hub2 | 202.6796 | 388328.6849 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX pump ETS | Conversion | hub3 | 40.274 | 342043.0762 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX pump ETS | Conversion | hub4 | 185.968 | 383565.8917 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX pump ETS | Conversion | hub5 | 89.6684 | 356120.4814 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX pump ETS | Conversion | hub6 | 83.8601 | 354465.1173 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX pump ETS | Conversion | hub7 | 69.4998 | 350372.4299 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX pump ETS | Conversion | hub8 | 66.7487 | 349588.3658 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | HEX pump ETS | Conversion | hub9 | 463.7871 | 462744.3095 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Main HP | Conversion | plant | 1159.333 | 1890872.1756 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump DHW | Conversion | hub11 | 34.8297 | 6615.3189 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump DHW | Conversion | hub12 | 554.1475 | 8692.59 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump DHW | Conversion | hub4 | 94.6748 | 6854.6992 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump DHW | Conversion | hub5 | 55.1879 | 6696.7517 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump DHW | Conversion | hub7 | 43.6957 | 6650.7829 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump DHW | Conversion | hub8 | 43.6957 | 6650.7829 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump DHW | Conversion | hub9 | 71.4402 | 6761.7607 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump SH | Conversion | hub1 | 2304.5377 | 153051.434 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump SH | Conversion | hub10 | 135.9123 | 70643.6666 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump SH | Conversion | hub11 | 218.5355 | 73783.3473 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump SH | Conversion | hub12 | 2153.8699 | 147326.0568 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump SH | Conversion | hub13 | 140.401 | 70814.2363 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump SH | Conversion | hub14 | 142.1925 | 70882.315 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump SH | Conversion | hub2 | 279.8181 | 76112.0868 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump SH | Conversion | hub3 | 58.7399 | 67711.1175 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump SH | Conversion | hub4 | 273.5294 | 75873.1155 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump SH | Conversion | hub5 | 136.167 | 70653.3444 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump SH | Conversion | hub6 | 115.1239 | 69853.7071 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump SH | Conversion | hub7 | 104.0534 | 69433.0295 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump SH | Conversion | hub8 | 100.9653 | 69315.682 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump SH | Conversion | hub9 | 674.3585 | 91104.6234 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump cooling | Conversion | hub1 | 2746.524 | 128799.7209 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump cooling | Conversion | hub10 | 43.5653 | 47710.9591 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump cooling | Conversion | hub11 | 266.7618 | 54406.8527 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump cooling | Conversion | hub12 | 4679.9342 | 186802.0256 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump cooling | Conversion | hub13 | 151.9881 | 50963.6432 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump cooling | Conversion | hub14 | 103.6616 | 49513.8471 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump cooling | Conversion | hub2 | 326.6423 | 56203.2698 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump cooling | Conversion | hub3 | 100.4378 | 49417.1337 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump cooling | Conversion | hub4 | 748.031 | 68844.9301 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump cooling | Conversion | hub5 | 380.9923 | 57833.7705 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump cooling | Conversion | hub6 | 127.8045 | 50238.1341 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump cooling | Conversion | hub7 | 264.3832 | 54335.4958 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump cooling | Conversion | hub8 | 267.1967 | 54419.9003 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Pump cooling | Conversion | hub9 | 1086.2268 | 78990.8032 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | cooling tower plant | Conversion | plant | 1288.1478 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | parking to pv | Conversion | plant | 0.1 | 400 |  | 0 | 54.4563 | 0
Solution 2 | stage0 | stage0 | pv to electricity | Conversion | plant | 321.6684 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | pv to hub | Conversion | hub1 | 815.2307 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | pv to hub | Conversion | hub10 | 19.0762 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | pv to hub | Conversion | hub11 | 112.6625 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | pv to hub | Conversion | hub12 | 1539.7145 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | pv to hub | Conversion | hub13 | 14.2794 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | pv to hub | Conversion | hub14 | 12.1921 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | pv to hub | Conversion | hub2 | 73.8767 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | pv to hub | Conversion | hub3 | 62.3084 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | pv to hub | Conversion | hub4 | 143.4758 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | pv to hub | Conversion | hub5 | 79.0594 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | pv to hub | Conversion | hub6 | 71.9101 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | pv to hub | Conversion | hub7 | 57.1823 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | pv to hub | Conversion | hub8 | 60.1299 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | pv to hub | Conversion | hub9 | 330.3086 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | rooftop to pv | Conversion | plant | 3393.3764 | 11876817.3281 |  | 0 | 1616920.1946 | 0
Solution 2 | stage0 | stage0 | battery | Storage | plant | 0.1 | 75.7 | 15 | 56.7303 | 34.3529 | 0
Solution 2 | stage0 | stage0 | Generic Hot Water Storage hub1 | Storage | hub1 | 0.27028 | 13813.2437 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Generic Hot Water Storage hub2 | Storage | hub2 | 0.18177 | 13808.9069 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Generic Hot Water Storage hub3 | Storage | hub3 | 0.6601 | 13832.3451 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Generic Hot Water Storage hub4 | Storage | hub4 | 524.9076 | 39520.4742 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Generic Hot Water Storage hub5 | Storage | hub5 | 285.4266 | 27785.9036 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Generic Hot Water Storage hub6 | Storage | hub6 | 0.26712 | 13813.0891 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Generic Hot Water Storage hub7 | Storage | hub7 | 234.2861 | 25280.0185 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Generic Hot Water Storage hub8 | Storage | hub8 | 249.0893 | 26005.3734 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Generic Hot Water Storage hub9 | Storage | hub9 | 566.0698 | 41537.4203 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Generic Hot Water Storage hub10 | Storage | hub10 | 0.29546 | 13814.4778 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Generic Hot Water Storage hub11 | Storage | hub11 | 180.8518 | 22661.7363 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Generic Hot Water Storage hub12 | Storage | hub12 | 3173.3607 | 169294.676 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Generic Hot Water Storage hub13 | Storage | hub13 | 0.26628 | 13813.0477 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Generic Hot Water Storage hub14 | Storage | hub14 | 0.15992 | 13807.8361 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Generic Borehole | Storage | plant | 9500000 | 14250000 |  | 0 | 4850018.3459 | 0
Solution 2 | stage0 | stage0 | Anergy | Network | hub1_to_hub2_Anergy | 7736.5544 | 580800 |  | 0 | 197676.5372 | 0
Solution 2 | stage0 | stage0 | Anergy | Network | hub3_to_hub4_Anergy | 7406.4203 | 548900 |  | 0 | 186819.3032 | 0
Solution 2 | stage0 | stage0 | Anergy | Network | hub5_to_hub6_Anergy | 6508.4723 | 385000 |  | 0 | 131035.5834 | 0
Solution 2 | stage0 | stage0 | Anergy | Network | hub7_to_hub8_Anergy | 6240.8371 | 218900 |  | 0 | 74503.0888 | 0
Solution 2 | stage0 | stage0 | Anergy | Network | hub9_to_hub10_Anergy | 5029.6457 | 920700 |  | 0 | 313362.238 | 0
Solution 2 | stage0 | stage0 | Anergy | Network | hub11_to_hub12_Anergy | 4745.1749 | 718300 |  | 0 | 244474.9598 | 0
Solution 2 | stage0 | stage0 | Anergy | Network | hub13_to_hub14_Anergy | 113.8479 | 465300 |  | 0 | 158365.8622 | 0
Solution 2 | stage0 | stage0 | pv_loop | Network | hub1_to_hub2_pv_loop | 2262.8414 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | pv_loop | Network | hub3_to_hub4_pv_loop | 2203.5115 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | pv_loop | Network | hub5_to_hub6_pv_loop | 1985.0177 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | pv_loop | Network | hub7_to_hub8_pv_loop | 1927.1374 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | pv_loop | Network | hub9_to_hub10_pv_loop | 1622.6446 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | pv_loop | Network | hub11_to_hub12_pv_loop | 1540.416 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | pv_loop | Network | hub13_to_hub14_pv_loop | 12.1921 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | Anergy | Network | plant_to_hub1_Anergy | 10492.0879 | 114400 |  | 0 | 38936.2876 | 0
Solution 2 | stage0 | stage0 | Anergy | Network | hub2_to_hub3_Anergy | 7516.005 | 133100 |  | 0 | 45300.8731 | 0
Solution 2 | stage0 | stage0 | Anergy | Network | hub4_to_hub5_Anergy | 6748.5523 | 145200 |  | 0 | 49419.1343 | 0
Solution 2 | stage0 | stage0 | Anergy | Network | hub6_to_hub7_Anergy | 6415.7201 | 177100 |  | 0 | 60276.3684 | 0
Solution 2 | stage0 | stage0 | Anergy | Network | hub8_to_hub9_Anergy | 6098.6229 | 1534500 |  | 0 | 522270.3966 | 0
Solution 2 | stage0 | stage0 | Anergy | Network | hub10_to_hub11_Anergy | 4983.0873 | 174900 |  | 0 | 59527.5936 | 0
Solution 2 | stage0 | stage0 | Anergy | Network | hub12_to_hub13_Anergy | 228.6868 | 347600 |  | 0 | 118306.4124 | 0
Solution 2 | stage0 | stage0 | pv_loop | Network | plant_to_hub1_pv_loop | 3071.708 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | pv_loop | Network | hub2_to_hub3_pv_loop | 2239.6416 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | pv_loop | Network | hub4_to_hub5_pv_loop | 2061.665 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | pv_loop | Network | hub6_to_hub7_pv_loop | 1982.9516 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | pv_loop | Network | hub8_to_hub9_pv_loop | 1867.6478 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | pv_loop | Network | hub10_to_hub11_pv_loop | 1621.7903 | 0 |  | 0 | 0 | 0
Solution 2 | stage0 | stage0 | pv_loop | Network | hub12_to_hub13_pv_loop | 24.5549 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | ETS HP | Conversion | hub1 | 2942.74 | 6140570.2691 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | ETS HP | Conversion | hub10 | 46.7128 | 116833.6753 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | ETS HP | Conversion | hub11 | 304.4511 | 652929.3399 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | ETS HP | Conversion | hub12 | 5359.4493 | 11167325.4429 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | ETS HP | Conversion | hub13 | 162.8801 | 358461.6362 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | ETS HP | Conversion | hub14 | 111.1017 | 250762.5011 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | ETS HP | Conversion | hub2 | 350.0096 | 747691.0408 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | ETS HP | Conversion | hub3 | 107.6476 | 243578.0749 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | ETS HP | Conversion | hub4 | 843.4468 | 1774040.3228 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | ETS HP | Conversion | hub5 | 431.0509 | 916256.9715 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | ETS HP | Conversion | hub6 | 136.9691 | 304566.676 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | ETS HP | Conversion | hub7 | 301.8022 | 647419.5681 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | ETS HP | Conversion | hub8 | 305.5068 | 655125.059 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | ETS HP | Conversion | hub9 | 1205.2119 | 2526511.7518 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX SC ets | Conversion | hub1 | 8.8973 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX SC ets | Conversion | hub10 | 0.30656 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX SC ets | Conversion | hub11 | 0.59251 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX SC ets | Conversion | hub12 | 4.0488 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX SC ets | Conversion | hub13 | 0.46855 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX SC ets | Conversion | hub14 | 0.4369 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX SC ets | Conversion | hub2 | 1.1052 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX SC ets | Conversion | hub3 | 0.29564 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX SC ets | Conversion | hub4 | 1.3202 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX SC ets | Conversion | hub5 | 0.65858 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX SC ets | Conversion | hub6 | 0.44146 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX SC ets | Conversion | hub7 | 0.516 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX SC ets | Conversion | hub8 | 0.51751 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX SC ets | Conversion | hub9 | 3.0999 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX pump ETS | Conversion | hub1 | 1506.007 | 759776.9816 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX pump ETS | Conversion | hub10 | 106.6678 | 360965.3177 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX pump ETS | Conversion | hub11 | 167.9563 | 378432.5314 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX pump ETS | Conversion | hub12 | 1922.0431 | 878347.2886 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX pump ETS | Conversion | hub13 | 104.7669 | 360423.5594 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX pump ETS | Conversion | hub14 | 107.4477 | 361187.5877 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX pump ETS | Conversion | hub2 | 202.6796 | 388328.6849 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX pump ETS | Conversion | hub3 | 40.274 | 342043.0762 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX pump ETS | Conversion | hub4 | 189.4114 | 384547.2364 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX pump ETS | Conversion | hub5 | 94.0818 | 357378.3082 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX pump ETS | Conversion | hub6 | 83.8601 | 354465.1173 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX pump ETS | Conversion | hub7 | 71.1854 | 350852.8324 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX pump ETS | Conversion | hub8 | 68.4318 | 350068.0583 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | HEX pump ETS | Conversion | hub9 | 460.6506 | 461850.4327 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Main HP | Conversion | plant | 1353.2326 | 2207122.3652 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump DHW | Conversion | hub11 | 34.8297 | 6615.3189 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump DHW | Conversion | hub12 | 554.1475 | 8692.59 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump DHW | Conversion | hub4 | 94.6748 | 6854.6992 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump DHW | Conversion | hub5 | 55.1879 | 6696.7517 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump DHW | Conversion | hub7 | 43.6957 | 6650.7829 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump DHW | Conversion | hub8 | 43.6957 | 6650.7829 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump DHW | Conversion | hub9 | 71.4402 | 6761.7607 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump SH | Conversion | hub1 | 2304.5377 | 153051.434 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump SH | Conversion | hub10 | 135.9123 | 70643.6666 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump SH | Conversion | hub11 | 218.5355 | 73783.3473 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump SH | Conversion | hub12 | 2153.8699 | 147326.0568 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump SH | Conversion | hub13 | 140.401 | 70814.2363 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump SH | Conversion | hub14 | 142.1925 | 70882.315 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump SH | Conversion | hub2 | 279.8181 | 76112.0868 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump SH | Conversion | hub3 | 58.7399 | 67711.1175 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump SH | Conversion | hub4 | 273.5294 | 75873.1155 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump SH | Conversion | hub5 | 136.167 | 70653.3444 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump SH | Conversion | hub6 | 115.1239 | 69853.7071 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump SH | Conversion | hub7 | 104.0534 | 69433.0295 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump SH | Conversion | hub8 | 100.9653 | 69315.682 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump SH | Conversion | hub9 | 674.3585 | 91104.6234 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump cooling | Conversion | hub1 | 2746.524 | 128799.7209 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump cooling | Conversion | hub10 | 43.5653 | 47710.9591 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump cooling | Conversion | hub11 | 266.7618 | 54406.8527 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump cooling | Conversion | hub12 | 4679.9342 | 186802.0256 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump cooling | Conversion | hub13 | 151.9881 | 50963.6432 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump cooling | Conversion | hub14 | 103.6616 | 49513.8471 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump cooling | Conversion | hub2 | 326.6423 | 56203.2698 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump cooling | Conversion | hub3 | 100.4378 | 49417.1337 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump cooling | Conversion | hub4 | 748.031 | 68844.9301 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump cooling | Conversion | hub5 | 380.9923 | 57833.7705 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump cooling | Conversion | hub6 | 127.8045 | 50238.1341 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump cooling | Conversion | hub7 | 264.3832 | 54335.4958 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump cooling | Conversion | hub8 | 267.1967 | 54419.9003 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Pump cooling | Conversion | hub9 | 1086.2268 | 78990.8032 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | cooling tower plant | Conversion | plant | 1503.5918 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | parking to pv | Conversion | plant | 428.4382 | 1713752.9896 |  | 0 | 233311.8159 | 0
Solution 3 | stage0 | stage0 | pv to electricity | Conversion | plant | 421.0057 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | pv to hub | Conversion | hub1 | 1124.7082 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | pv to hub | Conversion | hub10 | 25.7761 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | pv to hub | Conversion | hub11 | 137.8182 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | pv to hub | Conversion | hub12 | 1831.8778 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | pv to hub | Conversion | hub13 | 38.7899 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | pv to hub | Conversion | hub14 | 58.1681 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | pv to hub | Conversion | hub2 | 96.0606 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | pv to hub | Conversion | hub3 | 87.7564 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | pv to hub | Conversion | hub4 | 236.1856 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | pv to hub | Conversion | hub5 | 114.7826 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | pv to hub | Conversion | hub6 | 72.5934 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | pv to hub | Conversion | hub7 | 85.116 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | pv to hub | Conversion | hub8 | 86.4032 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | pv to hub | Conversion | hub9 | 485.2683 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | rooftop to pv | Conversion | plant | 6584.7276 | 23046546.6 |  | 0 | 3137576.809 | 0
Solution 3 | stage0 | stage0 | battery | Storage | plant | 4551.1495 | 3445220.1647 | 15 | 2581878.8801 | 1563450.8542 | 0
Solution 3 | stage0 | stage0 | Generic Hot Water Storage hub1 | Storage | hub1 | 0.27028 | 13813.2437 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Generic Hot Water Storage hub2 | Storage | hub2 | 0.74387 | 13836.4499 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Generic Hot Water Storage hub3 | Storage | hub3 | 0.68698 | 13833.6618 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Generic Hot Water Storage hub4 | Storage | hub4 | 467.9774 | 36730.8933 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Generic Hot Water Storage hub5 | Storage | hub5 | 247.8556 | 25944.9247 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Generic Hot Water Storage hub6 | Storage | hub6 | 0.26712 | 13813.0891 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Generic Hot Water Storage hub7 | Storage | hub7 | 203.082 | 23751.0193 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Generic Hot Water Storage hub8 | Storage | hub8 | 213.6464 | 24268.6738 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Generic Hot Water Storage hub9 | Storage | hub9 | 501.8655 | 38391.4114 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Generic Hot Water Storage hub10 | Storage | hub10 | 0.42749 | 13820.9468 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Generic Hot Water Storage hub11 | Storage | hub11 | 203.0812 | 23750.9786 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Generic Hot Water Storage hub12 | Storage | hub12 | 4289.7861 | 223999.5185 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Generic Hot Water Storage hub13 | Storage | hub13 | 0.26628 | 13813.0477 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Generic Hot Water Storage hub14 | Storage | hub14 | 0.27028 | 13813.2437 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Generic Borehole | Storage | plant | 9500000 | 14250000 |  | 0 | 4850018.3459 | 0
Solution 3 | stage0 | stage0 | Anergy | Network | hub1_to_hub2_Anergy | 7902.4821 | 580800 |  | 0 | 197676.5372 | 0
Solution 3 | stage0 | stage0 | Anergy | Network | hub3_to_hub4_Anergy | 7557.5757 | 548900 |  | 0 | 186819.3032 | 0
Solution 3 | stage0 | stage0 | Anergy | Network | hub5_to_hub6_Anergy | 6447.1015 | 385000 |  | 0 | 131035.5834 | 0
Solution 3 | stage0 | stage0 | Anergy | Network | hub7_to_hub8_Anergy | 6228.776 | 218900 |  | 0 | 74503.0888 | 0
Solution 3 | stage0 | stage0 | Anergy | Network | hub9_to_hub10_Anergy | 4945.9411 | 920700 |  | 0 | 313362.238 | 0
Solution 3 | stage0 | stage0 | Anergy | Network | hub11_to_hub12_Anergy | 4654.5394 | 718300 |  | 0 | 244474.9598 | 0
Solution 3 | stage0 | stage0 | Anergy | Network | hub13_to_hub14_Anergy | 113.8479 | 465300 |  | 0 | 158365.8622 | 0
Solution 3 | stage0 | stage0 | pv_loop | Network | hub1_to_hub2_pv_loop | 3157.0146 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | pv_loop | Network | hub3_to_hub4_pv_loop | 2995.6954 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | pv_loop | Network | hub5_to_hub6_pv_loop | 2644.7272 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | pv_loop | Network | hub7_to_hub8_pv_loop | 2557.5667 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | pv_loop | Network | hub9_to_hub10_pv_loop | 2013.8056 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | pv_loop | Network | hub11_to_hub12_pv_loop | 1887.682 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | pv_loop | Network | hub13_to_hub14_pv_loop | 58.1681 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | Anergy | Network | plant_to_hub1_Anergy | 10658.0156 | 114400 |  | 0 | 38936.2876 | 0
Solution 3 | stage0 | stage0 | Anergy | Network | hub2_to_hub3_Anergy | 7667.1604 | 133100 |  | 0 | 45300.8731 | 0
Solution 3 | stage0 | stage0 | Anergy | Network | hub4_to_hub5_Anergy | 6813.0744 | 145200 |  | 0 | 49419.1343 | 0
Solution 3 | stage0 | stage0 | Anergy | Network | hub6_to_hub7_Anergy | 6436.5766 | 177100 |  | 0 | 60276.3684 | 0
Solution 3 | stage0 | stage0 | Anergy | Network | hub8_to_hub9_Anergy | 6063.1708 | 1534500 |  | 0 | 522270.3966 | 0
Solution 3 | stage0 | stage0 | Anergy | Network | hub10_to_hub11_Anergy | 4899.4487 | 174900 |  | 0 | 59527.5936 | 0
Solution 3 | stage0 | stage0 | Anergy | Network | hub12_to_hub13_Anergy | 228.6265 | 347600 |  | 0 | 118306.4124 | 0
Solution 3 | stage0 | stage0 | pv_loop | Network | plant_to_hub1_pv_loop | 4162.1831 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | pv_loop | Network | hub2_to_hub3_pv_loop | 3083.4519 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | pv_loop | Network | hub4_to_hub5_pv_loop | 2759.5098 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | pv_loop | Network | hub6_to_hub7_pv_loop | 2642.6827 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | pv_loop | Network | hub8_to_hub9_pv_loop | 2478.1452 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | pv_loop | Network | hub10_to_hub11_pv_loop | 1998.7284 | 0 |  | 0 | 0 | 0
Solution 3 | stage0 | stage0 | pv_loop | Network | hub12_to_hub13_pv_loop | 62.151 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | ETS HP | Conversion | hub1 | 2942.74 | 6140570.2691 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | ETS HP | Conversion | hub10 | 46.7179 | 116844.2072 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | ETS HP | Conversion | hub11 | 370.1519 | 789586.9534 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | ETS HP | Conversion | hub12 | 6233.1649 | 12984653.9312 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | ETS HP | Conversion | hub13 | 162.8801 | 358461.6362 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | ETS HP | Conversion | hub14 | 111.1017 | 250762.5011 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | ETS HP | Conversion | hub2 | 350.0096 | 747691.0408 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | ETS HP | Conversion | hub3 | 107.6476 | 243578.0749 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | ETS HP | Conversion | hub4 | 886.9535 | 1864534.2885 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | ETS HP | Conversion | hub5 | 458.0442 | 972402.9371 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | ETS HP | Conversion | hub6 | 136.9691 | 304566.676 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | ETS HP | Conversion | hub7 | 322.6838 | 690853.2358 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | ETS HP | Conversion | hub8 | 325.6982 | 697123.2814 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | ETS HP | Conversion | hub9 | 1228.2967 | 2574528.2277 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX SC ets | Conversion | hub1 | 8.8973 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX SC ets | Conversion | hub10 | 0.30656 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX SC ets | Conversion | hub11 | 0.35302 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX SC ets | Conversion | hub12 | 9.3523 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX SC ets | Conversion | hub13 | 0.37588 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX SC ets | Conversion | hub14 | 0.4369 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX SC ets | Conversion | hub2 | 0.45201 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX SC ets | Conversion | hub3 | 0.1 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX SC ets | Conversion | hub4 | 0.54157 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX SC ets | Conversion | hub5 | 0.51606 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX SC ets | Conversion | hub6 | 0.18597 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX SC ets | Conversion | hub7 | 0.56142 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX SC ets | Conversion | hub8 | 0.59486 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX SC ets | Conversion | hub9 | 1.6167 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX pump ETS | Conversion | hub1 | 1506.007 | 759776.9816 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX pump ETS | Conversion | hub10 | 106.6678 | 360965.3177 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX pump ETS | Conversion | hub11 | 176.5094 | 380870.1805 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX pump ETS | Conversion | hub12 | 2748.1068 | 1113775.4484 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX pump ETS | Conversion | hub13 | 108.0765 | 361366.8039 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX pump ETS | Conversion | hub14 | 107.4477 | 361187.5877 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX pump ETS | Conversion | hub2 | 226.0069 | 394976.968 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX pump ETS | Conversion | hub3 | 47.2552 | 344032.7304 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX pump ETS | Conversion | hub4 | 220.7909 | 393490.4176 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX pump ETS | Conversion | hub5 | 109.7622 | 361847.2191 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX pump ETS | Conversion | hub6 | 92.9847 | 357065.6298 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX pump ETS | Conversion | hub7 | 83.6398 | 354402.3329 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX pump ETS | Conversion | hub8 | 82.0974 | 353962.7634 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | HEX pump ETS | Conversion | hub9 | 513.6232 | 476947.5998 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Main HP | Conversion | plant | 3622.395 | 5908126.1915 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump DHW | Conversion | hub11 | 34.8297 | 6615.3189 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump DHW | Conversion | hub12 | 554.1475 | 8692.59 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump DHW | Conversion | hub4 | 94.6748 | 6854.6992 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump DHW | Conversion | hub5 | 55.1879 | 6696.7517 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump DHW | Conversion | hub7 | 43.6957 | 6650.7829 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump DHW | Conversion | hub8 | 43.6957 | 6650.7829 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump DHW | Conversion | hub9 | 71.4402 | 6761.7607 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump SH | Conversion | hub1 | 2304.5377 | 153051.434 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump SH | Conversion | hub10 | 135.9123 | 70643.6666 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump SH | Conversion | hub11 | 218.5355 | 73783.3473 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump SH | Conversion | hub12 | 2153.8699 | 147326.0568 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump SH | Conversion | hub13 | 140.401 | 70814.2363 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump SH | Conversion | hub14 | 142.1925 | 70882.315 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump SH | Conversion | hub2 | 279.8181 | 76112.0868 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump SH | Conversion | hub3 | 58.7399 | 67711.1175 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump SH | Conversion | hub4 | 273.5294 | 75873.1155 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump SH | Conversion | hub5 | 136.167 | 70653.3444 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump SH | Conversion | hub6 | 115.1239 | 69853.7071 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump SH | Conversion | hub7 | 104.0534 | 69433.0295 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump SH | Conversion | hub8 | 100.9653 | 69315.682 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump SH | Conversion | hub9 | 674.3585 | 91104.6234 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump cooling | Conversion | hub1 | 2746.524 | 128799.7209 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump cooling | Conversion | hub10 | 43.5653 | 47710.9591 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump cooling | Conversion | hub11 | 266.7618 | 54406.8527 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump cooling | Conversion | hub12 | 4679.9342 | 186802.0256 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump cooling | Conversion | hub13 | 151.9881 | 50963.6432 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump cooling | Conversion | hub14 | 103.6616 | 49513.8471 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump cooling | Conversion | hub2 | 326.6423 | 56203.2698 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump cooling | Conversion | hub3 | 100.4378 | 49417.1337 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump cooling | Conversion | hub4 | 748.031 | 68844.9301 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump cooling | Conversion | hub5 | 380.9923 | 57833.7705 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump cooling | Conversion | hub6 | 127.8045 | 50238.1341 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump cooling | Conversion | hub7 | 264.3832 | 54335.4958 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump cooling | Conversion | hub8 | 267.1967 | 54419.9003 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Pump cooling | Conversion | hub9 | 1086.2268 | 78990.8032 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | cooling tower plant | Conversion | plant | 4024.8833 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | parking to pv | Conversion | plant | 5043.6508 | 20174603.04 |  | 0 | 2746587.926 | 0
Solution 4 | stage0 | stage0 | pv to electricity | Conversion | plant | 1126.9673 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | pv to hub | Conversion | hub1 | 1584.2629 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | pv to hub | Conversion | hub10 | 35.0766 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | pv to hub | Conversion | hub11 | 191.9448 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | pv to hub | Conversion | hub12 | 2281.6613 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | pv to hub | Conversion | hub13 | 66.6593 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | pv to hub | Conversion | hub14 | 60.4908 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | pv to hub | Conversion | hub2 | 143.7961 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | pv to hub | Conversion | hub3 | 90.3808 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | pv to hub | Conversion | hub4 | 308.8689 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | pv to hub | Conversion | hub5 | 155.8117 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | pv to hub | Conversion | hub6 | 73.2644 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | pv to hub | Conversion | hub7 | 115.5563 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | pv to hub | Conversion | hub8 | 104.0852 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | pv to hub | Conversion | hub9 | 774.5333 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | rooftop to pv | Conversion | plant | 6584.7276 | 23046546.6 |  | 0 | 3137576.809 | 0
Solution 4 | stage0 | stage0 | battery | Storage | plant | 8607 | 6515499 | 15 | 4882773.3663 | 2956752.251 | 0
Solution 4 | stage0 | stage0 | Generic Hot Water Storage hub1 | Storage | hub1 | 1.566 | 13876.736 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Generic Hot Water Storage hub2 | Storage | hub2 | 1.5659 | 13876.7273 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Generic Hot Water Storage hub3 | Storage | hub3 | 1.5465 | 13875.7803 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Generic Hot Water Storage hub4 | Storage | hub4 | 1139 | 69611 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Generic Hot Water Storage hub5 | Storage | hub5 | 664 | 46336 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Generic Hot Water Storage hub6 | Storage | hub6 | 1.4886 | 13872.9437 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Generic Hot Water Storage hub7 | Storage | hub7 | 525 | 39525 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Generic Hot Water Storage hub8 | Storage | hub8 | 525 | 39525 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Generic Hot Water Storage hub9 | Storage | hub9 | 859 | 55891 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Generic Hot Water Storage hub10 | Storage | hub10 | 1.5382 | 13875.3742 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Generic Hot Water Storage hub11 | Storage | hub11 | 633 | 44817 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Generic Hot Water Storage hub12 | Storage | hub12 | 11220 | 563580 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Generic Hot Water Storage hub13 | Storage | hub13 | 1.5574 | 13876.3132 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Generic Hot Water Storage hub14 | Storage | hub14 | 1.5299 | 13874.9638 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Generic Borehole | Storage | plant | 9500000 | 14250000 |  | 0 | 4850018.3459 | 0
Solution 4 | stage0 | stage0 | Anergy | Network | hub1_to_hub2_Anergy | 7439.1284 | 580800 |  | 0 | 197676.5372 | 0
Solution 4 | stage0 | stage0 | Anergy | Network | hub3_to_hub4_Anergy | 7235.0015 | 548900 |  | 0 | 186819.3032 | 0
Solution 4 | stage0 | stage0 | Anergy | Network | hub5_to_hub6_Anergy | 6244.1562 | 385000 |  | 0 | 131035.5834 | 0
Solution 4 | stage0 | stage0 | Anergy | Network | hub7_to_hub8_Anergy | 6026.3933 | 218900 |  | 0 | 74503.0888 | 0
Solution 4 | stage0 | stage0 | Anergy | Network | hub9_to_hub10_Anergy | 4827.6466 | 920700 |  | 0 | 313362.238 | 0
Solution 4 | stage0 | stage0 | Anergy | Network | hub11_to_hub12_Anergy | 4542.6692 | 718300 |  | 0 | 244474.9598 | 0
Solution 4 | stage0 | stage0 | Anergy | Network | hub13_to_hub14_Anergy | 113.8479 | 465300 |  | 0 | 158365.8622 | 0
Solution 4 | stage0 | stage0 | pv_loop | Network | hub1_to_hub2_pv_loop | 4372.8725 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | pv_loop | Network | hub3_to_hub4_pv_loop | 4138.6957 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | pv_loop | Network | hub5_to_hub6_pv_loop | 3674.0152 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | pv_loop | Network | hub7_to_hub8_pv_loop | 3485.1945 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | pv_loop | Network | hub9_to_hub10_pv_loop | 2612.4803 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | pv_loop | Network | hub11_to_hub12_pv_loop | 2388.2346 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | pv_loop | Network | hub13_to_hub14_pv_loop | 60.4908 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | Anergy | Network | plant_to_hub1_Anergy | 9948.7565 | 114400 |  | 0 | 38936.2876 | 0
Solution 4 | stage0 | stage0 | Anergy | Network | hub2_to_hub3_Anergy | 7344.5862 | 133100 |  | 0 | 45300.8731 | 0
Solution 4 | stage0 | stage0 | Anergy | Network | hub4_to_hub5_Anergy | 6570.8203 | 145200 |  | 0 | 49419.1343 | 0
Solution 4 | stage0 | stage0 | Anergy | Network | hub6_to_hub7_Anergy | 6244.1562 | 177100 |  | 0 | 60276.3684 | 0
Solution 4 | stage0 | stage0 | Anergy | Network | hub8_to_hub9_Anergy | 5805.5387 | 1534500 |  | 0 | 522270.3966 | 0
Solution 4 | stage0 | stage0 | Anergy | Network | hub10_to_hub11_Anergy | 4786.0131 | 174900 |  | 0 | 59527.5936 | 0
Solution 4 | stage0 | stage0 | Anergy | Network | hub12_to_hub13_Anergy | 228.5606 | 347600 |  | 0 | 118306.4124 | 0
Solution 4 | stage0 | stage0 | pv_loop | Network | plant_to_hub1_pv_loop | 5957.1355 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | pv_loop | Network | hub2_to_hub3_pv_loop | 4229.0765 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | pv_loop | Network | hub4_to_hub5_pv_loop | 3829.8268 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | pv_loop | Network | hub6_to_hub7_pv_loop | 3600.7508 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | pv_loop | Network | hub8_to_hub9_pv_loop | 3381.1092 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | pv_loop | Network | hub10_to_hub11_pv_loop | 2579.6258 | 0 |  | 0 | 0 | 0
Solution 4 | stage0 | stage0 | pv_loop | Network | hub12_to_hub13_pv_loop | 124.5007 | 0 |  | 0 | 0 | 0

## Capacity Limits
Solution | Stage | Name | Type | Hub or Link | Capacity (kW or KWh) | Min capacity (kW or KWh) | Max capacity (kW or KWh)
Solution 1 | stage0 | ETS HP Mode 2 | Conversion | hub1 | 0.1 | 0.1 | 1000000
Solution 1 | stage0 | ETS HP Mode 2 | Conversion | hub10 | 0.1 | 0.1 | 1000000
Solution 1 | stage0 | ETS HP Mode 2 | Conversion | hub13 | 0.1 | 0.1 | 1000000
Solution 1 | stage0 | ETS HP Mode 2 | Conversion | hub14 | 0.1 | 0.1 | 1000000
Solution 1 | stage0 | ETS HP Mode 2 | Conversion | hub2 | 0.1 | 0.1 | 1000000
Solution 1 | stage0 | ETS HP Mode 2 | Conversion | hub3 | 0.1 | 0.1 | 1000000
Solution 1 | stage0 | ETS HP Mode 2 | Conversion | hub6 | 0.1 | 0.1 | 1000000
Solution 1 | stage0 | Main HP Mode 1 | Conversion | plant | 0.1 | 0.1 | 1000000
Solution 1 | stage0 | cooling tower plant Mode 1 | Conversion | plant | 0.1 | 0.1 | 1000000
Solution 1 | stage0 | pv to hub Mode 1 | Conversion | hub13 | 0.1 | 0.1 | 1000000
Solution 1 | stage0 | pv to hub Mode 1 | Conversion | hub7 | 0.1 | 0.1 | 1000000
Solution 1 | stage0 | Generic Borehole | Storage | plant | 9500000 | 0.1 | 9500000
Solution 2 | stage0 | ETS HP Mode 2 | Conversion | hub1 | 0.1 | 0.1 | 1000000
Solution 2 | stage0 | ETS HP Mode 2 | Conversion | hub10 | 0.1 | 0.1 | 1000000
Solution 2 | stage0 | ETS HP Mode 2 | Conversion | hub13 | 0.1 | 0.1 | 1000000
Solution 2 | stage0 | ETS HP Mode 2 | Conversion | hub14 | 0.1 | 0.1 | 1000000
Solution 2 | stage0 | ETS HP Mode 2 | Conversion | hub2 | 0.1 | 0.1 | 1000000
Solution 2 | stage0 | ETS HP Mode 2 | Conversion | hub3 | 0.1 | 0.1 | 1000000
Solution 2 | stage0 | ETS HP Mode 2 | Conversion | hub6 | 0.1 | 0.1 | 1000000
Solution 2 | stage0 | Main HP Mode 1 | Conversion | plant | 0.1 | 0.1 | 1000000
Solution 2 | stage0 | cooling tower plant Mode 1 | Conversion | plant | 0.1 | 0.1 | 1000000
Solution 2 | stage0 | parking to pv Mode 1 | Conversion | plant | 0.1 | 0.1 | 1000000
Solution 2 | stage0 | battery | Storage | plant | 0.1 | 0.1 | 8607
Solution 2 | stage0 | Generic Borehole | Storage | plant | 9500000 | 0.1 | 9500000
Solution 3 | stage0 | ETS HP Mode 2 | Conversion | hub1 | 0.1 | 0.1 | 1000000
Solution 3 | stage0 | ETS HP Mode 2 | Conversion | hub10 | 0.1 | 0.1 | 1000000
Solution 3 | stage0 | ETS HP Mode 2 | Conversion | hub13 | 0.1 | 0.1 | 1000000
Solution 3 | stage0 | ETS HP Mode 2 | Conversion | hub14 | 0.1 | 0.1 | 1000000
Solution 3 | stage0 | ETS HP Mode 2 | Conversion | hub2 | 0.1 | 0.1 | 1000000
Solution 3 | stage0 | ETS HP Mode 2 | Conversion | hub3 | 0.1 | 0.1 | 1000000
Solution 3 | stage0 | ETS HP Mode 2 | Conversion | hub6 | 0.1 | 0.1 | 1000000
Solution 3 | stage0 | Main HP Mode 1 | Conversion | plant | 0.1 | 0.1 | 1000000
Solution 3 | stage0 | cooling tower plant Mode 1 | Conversion | plant | 0.1 | 0.1 | 1000000
Solution 3 | stage0 | Generic Borehole | Storage | plant | 9500000 | 0.1 | 9500000
Solution 4 | stage0 | ETS HP Mode 2 | Conversion | hub1 | 0.1 | 0.1 | 1000000
Solution 4 | stage0 | ETS HP Mode 2 | Conversion | hub13 | 0.1 | 0.1 | 1000000
Solution 4 | stage0 | ETS HP Mode 2 | Conversion | hub14 | 0.1 | 0.1 | 1000000
Solution 4 | stage0 | ETS HP Mode 2 | Conversion | hub2 | 0.1 | 0.1 | 1000000
Solution 4 | stage0 | ETS HP Mode 2 | Conversion | hub3 | 0.1 | 0.1 | 1000000
Solution 4 | stage0 | ETS HP Mode 2 | Conversion | hub6 | 0.1 | 0.1 | 1000000
Solution 4 | stage0 | HEX SC ets Mode 1 | Conversion | hub3 | 0.1 | 0.1 | 1000000
Solution 4 | stage0 | Main HP Mode 1 | Conversion | plant | 0.1 | 0.1 | 1000000
Solution 4 | stage0 | cooling tower plant Mode 1 | Conversion | plant | 0.1 | 0.1 | 1000000
Solution 4 | stage0 | battery | Storage | plant | 8607 | 0.1 | 8607
Solution 4 | stage0 | Generic Hot Water Storage hub4 | Storage | hub4 | 1139 | 0.1 | 1139
Solution 4 | stage0 | Generic Hot Water Storage hub5 | Storage | hub5 | 664 | 0.1 | 664
Solution 4 | stage0 | Generic Hot Water Storage hub7 | Storage | hub7 | 525 | 0.1 | 525
Solution 4 | stage0 | Generic Hot Water Storage hub8 | Storage | hub8 | 525 | 0.1 | 525
Solution 4 | stage0 | Generic Hot Water Storage hub9 | Storage | hub9 | 859 | 0.1 | 859
Solution 4 | stage0 | Generic Hot Water Storage hub11 | Storage | hub11 | 633 | 0.1 | 633
Solution 4 | stage0 | Generic Hot Water Storage hub12 | Storage | hub12 | 11220 | 0.1 | 11220
Solution 4 | stage0 | Generic Borehole | Storage | plant | 9500000 | 0.1 | 9500000

## Imports
Solution | Name | Stage | Hub | Capacity (kW) | Imported energy (kWh/year) | Monthly capacity (kW)
Solution 1 | Gas | stage0 | hub10 | 0 | -9.0288e-12 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 1 | Gas | stage0 | hub8 | 0 | -1.6868e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 1 | Gas | stage0 | hub11 | 0.1 | -6.3971e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 1 | Gas | stage0 | hub7 | 0 | -1.6162e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 1 | Gas | stage0 | hub14 | 0.1 | -4.8499e-08 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 1 | Gas | stage0 | hub2 | 0.1 | -1.4495e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 1 | Gas | stage0 | hub3 | 0.1 | -8.2857e-12 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, -0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 1 | Gas | stage0 | hub4 | 0.1 | -4.5187e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 1 | Gas | stage0 | hub6 | 0.1 | -1.0451e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 1 | Gas | stage0 | hub1 | 0.1 | -1.3907e-10 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 1 | Gas | stage0 | hub13 | 0 | -1.1347e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 1 | Gas | stage0 | hub5 | 0.1 | -1.9972e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 1 | Gas | stage0 | hub9 | 0.1 | -1.0835e-10 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 1 | Gas | stage0 | hub12 | 0.1 | -1.2994e-09 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 1 | Heat ambient in | stage0 | plant | 0 | 0 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 1 | Electricity | stage0 | hub10 | 34.868 | 78608.4824 | 34.597, 20.782, 21.069, 18.059, 28.222, 31.366, 32.84, 34.868, 29.072, 18.457, 20.444, 20.782
Solution 1 | Electricity | stage0 | plant | 360.415 | 1412666.4401 | 191.668, 205.952, 205.952, 236.826, 321.431, 360.415, 360.415, 360.415, 321.431, 218.776, 218.776, 191.668
Solution 1 | Electricity | stage0 | hub8 | 194.677 | 354652.802 | 56.403, 60.393, 60.574, 72.777, 109.576, 147.87, 147.87, 194.677, 113.624, 73.125, 65.194, 54.304
Solution 1 | Electricity | stage0 | hub11 | 193.17 | 557713.6737 | 106.739, 104.789, 103.5, 117.669, 145.148, 170.691, 175.197, 193.17, 156.01, 103.875, 102.822, 104.789
Solution 1 | Electricity | stage0 | hub7 | 194.542 | 347928.8952 | 57.125, 55.819, 57.375, 74.345, 108.301, 148.078, 148.078, 194.542, 112.795, 71.716, 63.156, 55.178
Solution 1 | Electricity | stage0 | hub14 | 61.953 | 133278.6032 | 52.301, 36.829, 32.883, 23.808, 34.445, 48.987, 57.136, 61.953, 34.445, 23.798, 32.883, 36.829
Solution 1 | Electricity | stage0 | hub2 | 137.983 | 316929.226 | 96.774, 117.544, 83.736, 75.355, 97.707, 137.983, 137.983, 137.983, 100.556, 93.188, 86.848, 117.544
Solution 1 | Electricity | stage0 | hub3 | 90.172 | 439172.3066 | 62.795, 62.795, 60.618, 58.628, 78.474, 85.357, 86.591, 90.172, 79.622, 57.696, 56.645, 62.795
Solution 1 | Electricity | stage0 | hub4 | 497.738 | 937727.3119 | 154.942, 169.96, 169.96, 210.104, 305.449, 421.531, 421.531, 497.738, 317.88, 200.947, 178.826, 146.082
Solution 1 | Electricity | stage0 | hub6 | 55.045 | 40681.9814 | 33.739, 30.702, 24.762, 19.962, 26.009, 45.338, 49.098, 55.045, 29.234, 18.461, 24.762, 30.702
Solution 1 | Electricity | stage0 | hub1 | 1569.875 | 3163423.6601 | 1261.666, 856.997, 788.171, 887.374, 1284.891, 1537.649, 1537.832, 1569.875, 1297.644, 891.291, 848.331, 856.997
Solution 1 | Electricity | stage0 | hub13 | 71.947 | 105234.2544 | 53.901, 46.683, 44.046, 40.01, 51.452, 69.58, 70.82, 71.947, 51.452, 40.004, 43.993, 46.683
Solution 1 | Electricity | stage0 | hub5 | 281.684 | 534771.5094 | 94.074, 94.992, 98.475, 119.679, 167.046, 234.239, 234.239, 281.684, 177.277, 114.385, 107.73, 89.296
Solution 1 | Electricity | stage0 | hub9 | 807.033 | 2471877.2612 | 439.478, 389.375, 463.8, 390.241, 557.093, 684.342, 684.342, 807.033, 568.554, 361.996, 362.11, 389.375
Solution 1 | Electricity | stage0 | hub12 | 2168.04 | 10689985.3595 | 1351.454, 1351.059, 1351.059, 1473.785, 1766.85, 2053.279, 2109.087, 2168.04, 1886.0, 1474.248, 1351.059, 1351.059
Solution 2 | Gas | stage0 | hub10 | 0 | -9.0288e-12 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 2 | Gas | stage0 | hub8 | 0 | -1.6924e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 2 | Gas | stage0 | hub11 | 0 | -6.3971e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 2 | Gas | stage0 | hub7 | 0 | -1.6162e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 2 | Gas | stage0 | hub14 | 0 | -2.3684e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 2 | Gas | stage0 | hub2 | 0 | -1.4495e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 2 | Gas | stage0 | hub3 | 0 | -8.4008e-12 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, -0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 2 | Gas | stage0 | hub4 | 0 | -4.5631e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 2 | Gas | stage0 | hub6 | 0 | -1.0923e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 2 | Gas | stage0 | hub1 | 0 | -1.3907e-10 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 2 | Gas | stage0 | hub13 | 0 | -1.1596e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 2 | Gas | stage0 | hub5 | 0 | -1.9972e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 2 | Gas | stage0 | hub9 | 0 | -1.0835e-10 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 2 | Gas | stage0 | hub12 | 0 | -1.3003e-09 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 2 | Heat ambient in | stage0 | plant | 0 | 0 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 2 | Electricity | stage0 | hub10 | 34.597 | 43730.1641 | 34.597, 20.782, 21.069, 18.059, 15.011, 16.805, 17.981, 22.536, 15.011, 18.457, 20.444, 20.782
Solution 2 | Electricity | stage0 | plant | 360.681 | 1123880.7842 | 206.104, 206.104, 206.104, 237.001, 321.668, 360.681, 360.681, 360.681, 321.668, 218.938, 218.938, 202.96
Solution 2 | Electricity | stage0 | hub8 | 188.282 | 232639.4666 | 56.716, 54.304, 55.355, 68.062, 107.785, 128.418, 139.857, 188.282, 114.105, 71.562, 64.15, 54.324
Solution 2 | Electricity | stage0 | hub11 | 160.857 | 292582.2931 | 105.997, 104.604, 100.321, 99.735, 89.444, 109.965, 124.503, 160.857, 106.472, 100.321, 100.321, 104.604
Solution 2 | Electricity | stage0 | hub7 | 187.8 | 254894.9404 | 57.361, 55.178, 56.759, 67.088, 106.339, 128.34, 138.614, 187.8, 112.795, 71.716, 62.667, 55.178
Solution 2 | Electricity | stage0 | hub14 | 53.115 | 108537.2486 | 52.301, 36.829, 32.883, 23.808, 25.797, 41.719, 48.299, 53.115, 25.797, 23.798, 32.883, 36.829
Solution 2 | Electricity | stage0 | hub2 | 137.983 | 259137.5746 | 96.774, 117.544, 83.736, 62.584, 95.678, 137.983, 137.983, 137.983, 95.678, 93.188, 86.848, 117.544
Solution 2 | Electricity | stage0 | hub3 | 85.766 | 304119.2277 | 60.692, 54.653, 59.888, 58.245, 69.514, 82.489, 82.489, 85.766, 77.346, 55.943, 55.603, 54.653
Solution 2 | Electricity | stage0 | hub4 | 486.867 | 904563.6738 | 154.981, 147.095, 150.526, 194.682, 282.465, 350.762, 364.448, 486.867, 302.49, 200.98, 176.828, 147.214
Solution 2 | Electricity | stage0 | hub6 | 23.418 | 18572.928 | 22.441, 23.418, 21.521, 2.458, 2.458, 0.671, 0.584, 1.354, 2.458, 18.223, 18.223, 23.418
Solution 2 | Electricity | stage0 | hub1 | 1375.561 | 2582709.0745 | 1261.666, 856.997, 788.171, 799.208, 964.69, 1375.561, 1375.561, 1375.561, 970.714, 800.82, 724.458, 856.997
Solution 2 | Electricity | stage0 | hub13 | 71.947 | 85823.9603 | 46.577, 45.955, 43.319, 40.01, 51.452, 69.58, 70.82, 71.947, 51.452, 40.004, 43.266, 45.955
Solution 2 | Electricity | stage0 | hub5 | 276.986 | 525209.1794 | 94.233, 95.9, 98.375, 118.619, 168.627, 199.49, 227.24, 276.986, 178.113, 114.385, 107.73, 88.877
Solution 2 | Electricity | stage0 | hub9 | 671.026 | 2332820.9897 | 439.534, 389.431, 463.856, 367.064, 463.78, 588.717, 622.371, 671.026, 499.602, 349.833, 362.11, 389.431
Solution 2 | Electricity | stage0 | hub12 | 2041.802 | 8180837.2747 | 1340.241, 1313.545, 1338.49, 1296.385, 1612.977, 1896.134, 1972.283, 2041.802, 1786.281, 1475.679, 1289.012, 1320.414
Solution 3 | Gas | stage0 | hub10 | 0 | -9.0288e-12 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 3 | Gas | stage0 | hub8 | 0 | -2.3061e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 3 | Gas | stage0 | hub11 | 0 | -7.323e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 3 | Gas | stage0 | hub7 | 0 | -1.6301e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 3 | Gas | stage0 | hub14 | 0 | -2.3684e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 3 | Gas | stage0 | hub2 | 0 | -1.4495e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 3 | Gas | stage0 | hub3 | 0 | -9.4532e-12 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, -0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 3 | Gas | stage0 | hub4 | 0 | -5.9756e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 3 | Gas | stage0 | hub6 | 0 | -1.5701e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 3 | Gas | stage0 | hub1 | 0 | -1.4507e-10 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 3 | Gas | stage0 | hub13 | 0 | -1.8501e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 3 | Gas | stage0 | hub5 | 0 | -2.0083e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 3 | Gas | stage0 | hub9 | 0 | -1.225e-10 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 3 | Gas | stage0 | hub12 | 0.1 | -1.3144e-09 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 3 | Heat ambient in | stage0 | plant | 0 | 0 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 3 | Electricity | stage0 | hub10 | 34.597 | 25589.321 | 34.597, 20.782, 21.069, 18.059, 15.011, 14.296, 17.067, 19.915, 15.011, 18.457, 20.444, 20.782
Solution 3 | Electricity | stage0 | plant | 375.468 | 793275.2943 | 240.575, 240.575, 240.575, 276.639, 375.468, 375.468, 345.576, 345.576, 375.468, 255.555, 255.555, 186.0
Solution 3 | Electricity | stage0 | hub8 | 138.241 | 180580.3392 | 57.319, 54.561, 57.645, 61.75, 93.268, 117.622, 121.926, 138.241, 100.978, 58.143, 54.163, 55.257
Solution 3 | Electricity | stage0 | hub11 | 136.919 | 256152.1914 | 105.27, 103.877, 99.593, 99.007, 87.659, 112.281, 124.503, 136.919, 103.283, 99.593, 99.593, 103.877
Solution 3 | Electricity | stage0 | hub7 | 138.619 | 191396.4472 | 57.965, 55.178, 57.031, 60.954, 93.18, 117.779, 122.007, 138.619, 100.511, 56.249, 51.817, 55.907
Solution 3 | Electricity | stage0 | hub14 | 52.301 | 55213.6291 | 52.301, 36.829, 32.883, 23.808, 15.261, 29.072, 33.483, 41.822, 21.342, 23.798, 32.883, 36.829
Solution 3 | Electricity | stage0 | hub2 | 137.983 | 166767.2281 | 96.774, 117.544, 83.736, 62.584, 95.678, 137.983, 137.983, 137.983, 95.678, 93.188, 86.848, 117.544
Solution 3 | Electricity | stage0 | hub3 | 82.633 | 246573.5621 | 60.692, 54.653, 59.888, 49.596, 64.139, 75.626, 78.851, 82.633, 69.862, 51.869, 53.125, 54.653
Solution 3 | Electricity | stage0 | hub4 | 375.738 | 745256.8058 | 156.215, 146.082, 147.632, 165.65, 251.324, 321.785, 329.584, 375.738, 272.025, 151.014, 145.801, 146.082
Solution 3 | Electricity | stage0 | hub6 | 23.418 | 11019.3448 | 22.441, 23.418, 21.521, 2.458, 2.458, 0.671, 0.479, 0.671, 2.458, 18.2, 18.2, 23.418
Solution 3 | Electricity | stage0 | hub1 | 1375.562 | 1894656.2825 | 1261.666, 856.997, 788.171, 799.208, 964.69, 1375.562, 1375.562, 1375.562, 970.688, 800.82, 724.458, 856.997
Solution 3 | Electricity | stage0 | hub13 | 71.947 | 45229.584 | 46.314, 45.692, 43.055, 40.01, 51.452, 69.58, 70.82, 71.947, 51.452, 40.004, 43.002, 45.692
Solution 3 | Electricity | stage0 | hub5 | 225.871 | 427185.5012 | 95.41, 88.297, 90.588, 100.78, 150.994, 183.253, 190.975, 225.871, 161.218, 91.042, 90.247, 88.297
Solution 3 | Electricity | stage0 | hub9 | 622.099 | 1897394.1274 | 442.592, 392.489, 466.914, 342.794, 430.025, 516.551, 549.17, 622.099, 472.854, 348.678, 362.11, 392.489
Solution 3 | Electricity | stage0 | hub12 | 2033.781 | 5979176.1339 | 1331.793, 1289.012, 1289.012, 1315.595, 1547.296, 1844.552, 1956.994, 2033.781, 1728.954, 1495.002, 1289.012, 1286.59
Solution 4 | Gas | stage0 | hub10 | 0 | -9.0566e-12 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 4 | Gas | stage0 | hub8 | 0 | -1.734e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 4 | Gas | stage0 | hub11 | 0 | -6.4165e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 4 | Gas | stage0 | hub7 | 0 | -1.6468e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 4 | Gas | stage0 | hub14 | 0 | -2.3684e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 4 | Gas | stage0 | hub2 | 0 | -1.4717e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 4 | Gas | stage0 | hub3 | 0 | -8.3481e-12 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, -0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 4 | Gas | stage0 | hub4 | 0 | -4.6519e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 4 | Gas | stage0 | hub6 | 0 | -1.0562e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 4 | Gas | stage0 | hub1 | 0 | -1.3907e-10 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 4 | Gas | stage0 | hub13 | 0 | -1.2346e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 4 | Gas | stage0 | hub5 | 0 | -2.0583e-11 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 4 | Gas | stage0 | hub9 | 0 | -1.0868e-10 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 4 | Gas | stage0 | hub12 | 0 | -1.2994e-09 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 4 | Heat ambient in | stage0 | plant | 0 | 0 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 4 | Electricity | stage0 | hub10 | 34.597 | 31893.9532 | 34.597, 18.457, 18.457, 18.059, 13.198, 13.18, 17.067, 17.738, 10.804, 18.457, 18.457, 12.431
Solution 4 | Electricity | stage0 | plant | 0 | 0 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 4 | Electricity | stage0 | hub8 | 134.745 | 157370.0444 | 55.939, 54.304, 50.263, 54.179, 88.623, 113.926, 118.23, 134.745, 97.481, 54.516, 52.273, 54.304
Solution 4 | Electricity | stage0 | hub11 | 139.166 | 200714.9558 | 46.027, 38.52, 36.819, 60.671, 81.388, 108.579, 121.731, 139.166, 97.64, 59.775, 46.144, 38.52
Solution 4 | Electricity | stage0 | hub7 | 135.295 | 149128.4981 | 57.028, 55.178, 50.345, 53.654, 87.971, 114.082, 118.311, 135.295, 97.014, 53.731, 51.488, 55.178
Solution 4 | Electricity | stage0 | hub14 | 52.301 | 61849.9202 | 52.301, 31.327, 27.864, 19.37, 15.261, 29.072, 33.483, 41.822, 21.342, 21.608, 26.925, 31.327
Solution 4 | Electricity | stage0 | hub2 | 93.188 | 106393.6689 | 86.809, 86.909, 83.736, 62.584, 52.894, 32.11, 50.556, 50.556, 23.193, 93.188, 85.894, 86.909
Solution 4 | Electricity | stage0 | hub3 | 82.633 | 181052.0591 | 52.155, 50.723, 52.455, 47.016, 64.139, 75.626, 78.851, 82.633, 69.862, 46.831, 47.175, 50.723
Solution 4 | Electricity | stage0 | hub4 | 368.162 | 374075.0189 | 150.468, 146.082, 132.209, 149.114, 241.631, 313.776, 322.835, 368.162, 264.45, 156.633, 138.832, 146.082
Solution 4 | Electricity | stage0 | hub6 | 22.081 | 11722.4123 | 22.081, 22.081, 21.476, 0.671, 0.671, 0.379, 0.379, 0.379, 0.671, 0.671, 17.851, 22.081
Solution 4 | Electricity | stage0 | hub1 | 1261.666 | 1020324.977 | 1261.666, 856.997, 788.171, 799.208, 751.195, 918.713, 1035.076, 1035.076, 645.706, 800.82, 724.458, 856.997
Solution 4 | Electricity | stage0 | hub13 | 42.462 | 47770.36 | 42.462, 42.187, 42.01, 40.01, 16.742, 42.462, 42.462, 42.462, 16.742, 40.004, 41.999, 42.187
Solution 4 | Electricity | stage0 | hub5 | 221.455 | 237553.7214 | 90.577, 87.834, 81.206, 91.782, 143.906, 178.584, 186.306, 221.455, 156.802, 91.042, 88.64, 87.834
Solution 4 | Electricity | stage0 | hub9 | 616.383 | 1075168.0672 | 322.359, 348.678, 348.678, 342.794, 424.308, 515.293, 543.127, 616.383, 467.138, 348.678, 348.678, 286.547
Solution 4 | Electricity | stage0 | hub12 | 2049.429 | 4925855.1478 | 1273.562, 1262.277, 1261.685, 1192.909, 1492.311, 1799.938, 1922.286, 2049.429, 1682.234, 1348.127, 1258.34, 1262.757

## Exports
Solution | Name | Stage | Hub | Capacity (kW) | Exported energy (kWh/year) | Monthly capacity (kW)
Solution 1 | Slack | stage0 | hub10 | 0.307 | 83.9044 | 0.307, 0.085, 0.088, 0.065, 0.028, 0.0, 0.0, 0.0, 0.0, 0.068, 0.083, 0.085
Solution 1 | Slack | stage0 | hub8 | 0.589 | 227.6923 | 0.589, 0.589, 0.436, 0.131, 0.015, 0.011, 0.0, 0.0, 0.0, 0.131, 0.132, 0.589
Solution 1 | Slack | stage0 | hub11 | 0.613 | 503.1105 | 0.603, 0.569, 0.613, 0.453, 0.327, 0.045, 0.0, 0.09, 0.29, 0.467, 0.529, 0.569
Solution 1 | Slack | stage0 | hub7 | 0.582 | 246.7497 | 0.582, 0.582, 0.405, 0.138, 0.016, 0.011, 0.0, 0.0, 0.0, 0.138, 0.138, 0.582
Solution 1 | Slack | stage0 | hub14 | 0.437 | 216.1493 | 0.437, 0.192, 0.162, 0.094, 0.04, 0.04, 0.0, 0.0, 0.017, 0.111, 0.162, 0.192
Solution 1 | Slack | stage0 | hub2 | 1.105 | 140.1151 | 0.602, 1.105, 0.391, 0.23, 0.0, 0.0, 0.0, 0.0, 0.0, 0.231, 0.435, 1.105
Solution 1 | Slack | stage0 | hub3 | 0.296 | 79.1141 | 0.29, 0.29, 0.296, 0.042, 0.007, 0.0, 0.002, 0.0, 0.002, 0.052, 0.071, 0.29
Solution 1 | Slack | stage0 | hub4 | 1.42 | 603.3812 | 1.42, 1.42, 1.106, 0.356, 0.045, 0.035, 0.0, 0.0, 0.0, 0.356, 0.372, 1.42
Solution 1 | Slack | stage0 | hub6 | 0.441 | 106.3127 | 0.441, 0.159, 0.157, 0.098, 0.028, 0.0, 0.0, 0.0, 0.0, 0.105, 0.131, 0.159
Solution 1 | Slack | stage0 | hub1 | 8.897 | 768.9111 | 8.897, 2.917, 2.037, 0.945, 0.0, 0.0, 0.0, 0.0, 0.0, 0.917, 2.033, 2.917
Solution 1 | Slack | stage0 | hub13 | 0.497 | 122.6832 | 0.497, 0.322, 0.27, 0.207, 0.016, 0.0, 0.0, 0.0, 0.0, 0.207, 0.269, 0.322
Solution 1 | Slack | stage0 | hub5 | 0.795 | 293.6841 | 0.795, 0.795, 0.497, 0.178, 0.008, 0.003, 0.0, 0.0, 0.0, 0.161, 0.178, 0.795
Solution 1 | Slack | stage0 | hub9 | 3.01 | 965.4953 | 2.421, 1.213, 3.01, 0.689, 0.319, 0.096, 0.0, 0.0, 0.052, 0.698, 0.805, 1.213
Solution 1 | Slack | stage0 | hub12 | 3.834 | 10889.1353 | 3.834, 3.834, 3.834, 3.68, 2.058, 1.957, 0.0, 0.0, 1.915, 3.725, 3.834, 3.834
Solution 1 | Heat ambient out | stage0 | plant | 1287.197 | 7118778.9979 | 1197.926, 1287.197, 1287.197, 1287.197, 1287.197, 1287.197, 1287.197, 1287.197, 1287.197, 1287.197, 1287.197, 1197.926
Solution 1 | export_electricity | stage0 | plant | 0.1 | 0 | 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0, 0.0
Solution 2 | Slack | stage0 | hub10 | 0.307 | 83.9112 | 0.307, 0.085, 0.088, 0.065, 0.028, 0.0, 0.0, 0.0, 0.0, 0.068, 0.083, 0.085
Solution 2 | Slack | stage0 | hub8 | 0.565 | 229.337 | 0.565, 0.565, 0.412, 0.132, 0.111, 0.099, 0.02, 0.0, 0.02, 0.132, 0.131, 0.565
Solution 2 | Slack | stage0 | hub11 | 0.613 | 503.439 | 0.603, 0.569, 0.613, 0.453, 0.327, 0.045, 0.0, 0.09, 0.262, 0.467, 0.529, 0.569
Solution 2 | Slack | stage0 | hub7 | 0.563 | 247.8541 | 0.563, 0.563, 0.387, 0.129, 0.108, 0.098, 0.021, 0.0, 0.021, 0.129, 0.138, 0.563
Solution 2 | Slack | stage0 | hub14 | 0.437 | 216.1531 | 0.437, 0.192, 0.162, 0.094, 0.04, 0.04, 0.0, 0.0, 0.017, 0.111, 0.162, 0.192
Solution 2 | Slack | stage0 | hub2 | 1.105 | 140.1187 | 0.602, 1.105, 0.391, 0.23, 0.0, 0.0, 0.0, 0.0, 0.0, 0.231, 0.435, 1.105
Solution 2 | Slack | stage0 | hub3 | 0.296 | 79.1189 | 0.29, 0.29, 0.296, 0.042, 0.007, 0.0, 0.002, 0.0, 0.002, 0.052, 0.071, 0.29
Solution 2 | Slack | stage0 | hub4 | 1.417 | 610.4638 | 1.417, 1.417, 1.103, 0.357, 0.248, 0.216, 0.019, 0.0, 0.019, 0.357, 0.364, 1.417
Solution 2 | Slack | stage0 | hub6 | 0.441 | 106.3182 | 0.441, 0.159, 0.157, 0.098, 0.028, 0.0, 0.0, 0.0, 0.0, 0.105, 0.131, 0.159
Solution 2 | Slack | stage0 | hub1 | 8.897 | 768.9166 | 8.897, 2.917, 2.037, 0.945, 0.0, 0.0, 0.0, 0.0, 0.0, 0.917, 2.033, 2.917
Solution 2 | Slack | stage0 | hub13 | 0.476 | 120.3074 | 0.476, 0.301, 0.249, 0.207, 0.016, 0.0, 0.0, 0.0, 0.0, 0.207, 0.248, 0.301
Solution 2 | Slack | stage0 | hub5 | 0.782 | 296.7717 | 0.782, 0.782, 0.485, 0.164, 0.132, 0.124, 0.0, 0.0, 0.0, 0.164, 0.179, 0.782
Solution 2 | Slack | stage0 | hub9 | 3.012 | 969.1649 | 2.423, 1.215, 3.012, 0.689, 0.319, 0.096, 0.0, 0.0, 0.052, 0.701, 0.805, 1.215
Solution 2 | Slack | stage0 | hub12 | 3.834 | 10908.0949 | 3.834, 3.834, 3.834, 3.701, 2.082, 2.082, 0.0, 0.0, 1.915, 3.758, 3.834, 3.834
Solution 2 | Heat ambient out | stage0 | plant | 1288.148 | 7118728.2661 | 1288.148, 1288.148, 1288.148, 1288.148, 1288.148, 1288.148, 1288.148, 1288.148, 1288.148, 1288.148, 1288.148, 1268.501
Solution 2 | export_electricity | stage0 | plant | 831.718 | 42177.4674 | 358.641, 358.641, 358.641, 831.718, 831.718, 831.718, 232.566, 0.0, 232.566, 0.0, 72.431, 0.0
Solution 3 | Slack | stage0 | hub10 | 0.307 | 83.9195 | 0.307, 0.085, 0.088, 0.065, 0.028, 0.0, 0.0, 0.0, 0.0, 0.068, 0.083, 0.085
Solution 3 | Slack | stage0 | hub8 | 0.518 | 226.3644 | 0.518, 0.518, 0.365, 0.088, 0.048, 0.041, 0.0, 0.0, 0.048, 0.093, 0.136, 0.518
Solution 3 | Slack | stage0 | hub11 | 0.593 | 505.2353 | 0.582, 0.548, 0.593, 0.432, 0.327, 0.045, 0.0, 0.09, 0.262, 0.446, 0.508, 0.548
Solution 3 | Slack | stage0 | hub7 | 0.516 | 246.4714 | 0.516, 0.516, 0.34, 0.114, 0.051, 0.038, 0.0, 0.0, 0.051, 0.098, 0.139, 0.516
Solution 3 | Slack | stage0 | hub14 | 0.437 | 216.1593 | 0.437, 0.192, 0.162, 0.094, 0.04, 0.04, 0.0, 0.0, 0.017, 0.111, 0.162, 0.192
Solution 3 | Slack | stage0 | hub2 | 1.105 | 140.1317 | 0.602, 1.105, 0.391, 0.23, 0.0, 0.0, 0.0, 0.0, 0.0, 0.231, 0.435, 1.105
Solution 3 | Slack | stage0 | hub3 | 0.296 | 79.1248 | 0.29, 0.29, 0.296, 0.042, 0.007, 0.0, 0.002, 0.0, 0.002, 0.052, 0.071, 0.29
Solution 3 | Slack | stage0 | hub4 | 1.32 | 605.2105 | 1.32, 1.32, 1.006, 0.253, 0.115, 0.061, 0.0, 0.0, 0.115, 0.257, 0.372, 1.32
Solution 3 | Slack | stage0 | hub6 | 0.441 | 106.3247 | 0.441, 0.159, 0.157, 0.098, 0.028, 0.0, 0.0, 0.0, 0.0, 0.105, 0.131, 0.159
Solution 3 | Slack | stage0 | hub1 | 8.897 | 768.9228 | 8.897, 2.917, 2.037, 0.945, 0.0, 0.0, 0.0, 0.0, 0.0, 0.917, 2.033, 2.917
Solution 3 | Slack | stage0 | hub13 | 0.469 | 119.6041 | 0.469, 0.293, 0.242, 0.207, 0.016, 0.0, 0.0, 0.0, 0.0, 0.207, 0.24, 0.293
Solution 3 | Slack | stage0 | hub5 | 0.659 | 290.3236 | 0.659, 0.659, 0.361, 0.146, 0.058, 0.045, 0.0, 0.0, 0.058, 0.115, 0.184, 0.659
Solution 3 | Slack | stage0 | hub9 | 3.1 | 972.6873 | 2.51, 1.302, 3.1, 0.689, 0.319, 0.096, 0.0, 0.0, 0.052, 0.698, 0.805, 1.302
Solution 3 | Slack | stage0 | hub12 | 4.049 | 10893.2441 | 3.844, 3.844, 4.049, 3.68, 2.247, 2.247, 0.0, 0.0, 2.183, 3.725, 3.844, 3.844
Solution 3 | Heat ambient out | stage0 | plant | 1503.592 | 7007857.6751 | 1503.592, 1503.592, 1503.592, 1503.592, 1503.592, 1503.592, 1503.592, 1503.592, 1503.592, 1503.592, 1503.592, 1162.501
Solution 3 | export_electricity | stage0 | plant | 2448.516 | 554771.5618 | 1078.175, 1078.175, 1078.175, 2448.516, 2448.516, 2448.516, 1211.762, 558.868, 1261.765, 468.889, 468.889, 0.0
Solution 4 | Slack | stage0 | hub10 | 0.307 | 83.9859 | 0.307, 0.085, 0.088, 0.065, 0.028, 0.0, 0.0, 0.0, 0.0, 0.068, 0.083, 0.085
Solution 4 | Slack | stage0 | hub8 | 0.595 | 255.0426 | 0.595, 0.595, 0.595, 0.135, 0.116, 0.109, 0.002, 0.002, 0.116, 0.135, 0.14, 0.595
Solution 4 | Slack | stage0 | hub11 | 0.353 | 519.7912 | 0.353, 0.353, 0.353, 0.351, 0.327, 0.045, 0.0, 0.09, 0.262, 0.343, 0.351, 0.353
Solution 4 | Slack | stage0 | hub7 | 0.561 | 276.3667 | 0.561, 0.561, 0.561, 0.135, 0.121, 0.108, 0.012, 0.012, 0.121, 0.135, 0.14, 0.561
Solution 4 | Slack | stage0 | hub14 | 0.437 | 216.2379 | 0.437, 0.192, 0.162, 0.094, 0.04, 0.04, 0.0, 0.0, 0.017, 0.111, 0.162, 0.192
Solution 4 | Slack | stage0 | hub2 | 0.452 | 137.3641 | 0.418, 0.452, 0.391, 0.23, 0.0, 0.0, 0.0, 0.0, 0.0, 0.231, 0.407, 0.452
Solution 4 | Slack | stage0 | hub3 | 0.1 | 71.8037 | 0.095, 0.095, 0.1, 0.042, 0.007, 0.0, 0.002, 0.0, 0.002, 0.052, 0.071, 0.095
Solution 4 | Slack | stage0 | hub4 | 0.542 | 635.9818 | 0.542, 0.542, 0.542, 0.297, 0.262, 0.209, 0.0, 0.0, 0.262, 0.297, 0.33, 0.542
Solution 4 | Slack | stage0 | hub6 | 0.186 | 105.3954 | 0.186, 0.159, 0.157, 0.098, 0.028, 0.0, 0.0, 0.0, 0.0, 0.105, 0.131, 0.159
Solution 4 | Slack | stage0 | hub1 | 8.897 | 768.9728 | 8.897, 2.917, 2.037, 0.945, 0.0, 0.0, 0.0, 0.0, 0.0, 0.917, 2.033, 2.917
Solution 4 | Slack | stage0 | hub13 | 0.376 | 116.9569 | 0.376, 0.215, 0.212, 0.207, 0.016, 0.0, 0.0, 0.0, 0.0, 0.207, 0.212, 0.215
Solution 4 | Slack | stage0 | hub5 | 0.516 | 330.001 | 0.516, 0.516, 0.516, 0.173, 0.149, 0.136, 0.016, 0.016, 0.149, 0.174, 0.176, 0.516
Solution 4 | Slack | stage0 | hub9 | 1.617 | 989.3864 | 1.027, 0.998, 1.617, 0.689, 0.319, 0.096, 0.0, 0.0, 0.052, 0.698, 0.863, 0.998
Solution 4 | Slack | stage0 | hub12 | 9.352 | 11327.9464 | 9.352, 9.352, 9.352, 4.476, 3.056, 2.828, 0.0, 0.0, 2.857, 5.101, 5.101, 9.352
Solution 4 | Heat ambient out | stage0 | plant | 4024.883 | 6746273.8336 | 4024.883, 4024.883, 4024.883, 4024.883, 4024.883, 4024.883, 4024.883, 4024.883, 4024.883, 4024.883, 4024.883, 4024.883
Solution 4 | export_electricity | stage0 | plant | 4397.082 | 2153708.0335 | 2048.902, 2048.902, 2048.902, 4397.082, 4397.082, 4397.082, 2813.558, 1897.072, 3518.977, 1201.501, 1201.501, 0.0

## On-site Resources
Solution | Stage | Name | Hub | Used energy (kWh/year) | Used resources
Solution 1 | stage0 | pv_parking | plant | 0 | 0
Solution 1 | stage0 | Solar Roof | plant | 101314.917 | 551.2022
Solution 2 | stage0 | pv_parking | plant | 132.034 | 0.71833
Solution 2 | stage0 | Solar Roof | plant | 4480410.884 | 24375.6025
Solution 3 | stage0 | pv_parking | plant | 565684.195 | 3077.5957
Solution 3 | stage0 | Solar Roof | plant | 8694079.85 | 47300
Solution 4 | stage0 | pv_parking | plant | 6659334.313 | 36230
Solution 4 | stage0 | Solar Roof | plant | 8694079.85 | 47300

## Conversions
Solution | Stage | Name | Hub | Mode | Capacity (kW_max) | Energy in (kWh/year) | Energy out (kWh/year) | Capacity factor
Solution 1 | stage0 | parking to pv | plant | parking to pv Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | cooling tower plant | plant | cooling tower plant Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | cooling tower plant | plant | cooling tower plant Mode 2 | 1287.1972 | 7118778.9979 | 7118778.9979 | 0.63133
Solution 1 | stage0 | pv to hub | hub1 | pv to hub Mode 1 | 37.6957 | 50503.9782 | 50503.9782 | 0.15294
Solution 1 | stage0 | pv to hub | hub10 | pv to hub Mode 1 | 0.66081 | 250.4488 | 250.4488 | 0.043253
Solution 1 | stage0 | pv to hub | hub11 | pv to hub Mode 1 | 2.9197 | 554.6758 | 554.6758 | 0.021685
Solution 1 | stage0 | pv to hub | hub12 | pv to hub Mode 1 | 5.003 | 963.0512 | 963.0512 | 0.021974
Solution 1 | stage0 | pv to hub | hub13 | pv to hub Mode 1 | 0.1 | 5.8 | 5.8 | 0.006621
Solution 1 | stage0 | pv to hub | hub14 | pv to hub Mode 1 | 3.3543 | 97.6379 | 97.6379 | 0.0033232
Solution 1 | stage0 | pv to hub | hub2 | pv to hub Mode 1 | 18.0835 | 14503.8945 | 14503.8945 | 0.091561
Solution 1 | stage0 | pv to hub | hub3 | pv to hub Mode 1 | 3.0233 | 4477.5216 | 4477.5216 | 0.16908
Solution 1 | stage0 | pv to hub | hub4 | pv to hub Mode 1 | 9.2811 | 2452.6017 | 2452.6017 | 0.030167
Solution 1 | stage0 | pv to hub | hub5 | pv to hub Mode 1 | 1.5814 | 932.1929 | 932.1929 | 0.067308
Solution 1 | stage0 | pv to hub | hub6 | pv to hub Mode 1 | 18.2194 | 25854.1881 | 25854.1881 | 0.162
Solution 1 | stage0 | pv to hub | hub7 | pv to hub Mode 1 | 0.1 | 16.4 | 16.4 | 0.018721
Solution 1 | stage0 | pv to hub | hub8 | pv to hub Mode 1 | 0.79303 | 58.7078 | 58.7078 | 0.0084512
Solution 1 | stage0 | pv to hub | hub9 | pv to hub Mode 1 | 5.003 | 643.8117 | 643.8117 | 0.01469
Solution 1 | stage0 | pv to electricity | plant | pv to electricity Mode 1 | 0.0005512 | 0.0066144 | 0.0066144 | 0
Solution 1 | stage0 | Pump DHW gas | hub1 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Pump DHW gas | hub10 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Pump DHW gas | hub11 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Pump DHW gas | hub12 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Pump DHW gas | hub13 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Pump DHW gas | hub14 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Pump DHW gas | hub2 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Pump DHW gas | hub3 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Pump DHW gas | hub4 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Pump DHW gas | hub5 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Pump DHW gas | hub6 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Pump DHW gas | hub7 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Pump DHW gas | hub8 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Pump DHW gas | hub9 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | HEX pump ETS | hub1 | HEX pump ETS Mode 1 | 1506.007 | 381512.9215 | 381512.9215 | 0.028919
Solution 1 | stage0 | HEX pump ETS | hub1 | HEX pump ETS Mode 2 | 3018.0923 | 2941029.9381 | 2941029.9381 | 0.11124
Solution 1 | stage0 | HEX pump ETS | hub10 | HEX pump ETS Mode 1 | 106.6678 | 41905.6002 | 41905.6002 | 0.044847
Solution 1 | stage0 | HEX pump ETS | hub10 | HEX pump ETS Mode 2 | 47.808 | 43951.8736 | 43951.8736 | 0.10495
Solution 1 | stage0 | HEX pump ETS | hub11 | HEX pump ETS Mode 1 | 167.2098 | 247090.4591 | 247090.4591 | 0.16869
Solution 1 | stage0 | HEX pump ETS | hub11 | HEX pump ETS Mode 2 | 251.7449 | 490647.0461 | 490647.0461 | 0.22249
Solution 1 | stage0 | HEX pump ETS | hub12 | HEX pump ETS Mode 1 | 1916.7844 | 5444567.6537 | 5444567.6537 | 0.32425
Solution 1 | stage0 | HEX pump ETS | hub12 | HEX pump ETS Mode 2 | 4523.195 | 7284626.1939 | 7284626.1939 | 0.18385
Solution 1 | stage0 | HEX pump ETS | hub13 | HEX pump ETS Mode 1 | 103.75 | 58147.5957 | 58147.5957 | 0.063979
Solution 1 | stage0 | HEX pump ETS | hub13 | HEX pump ETS Mode 2 | 166.954 | 76147.5729 | 76147.5729 | 0.052066
Solution 1 | stage0 | HEX pump ETS | hub14 | HEX pump ETS Mode 1 | 107.4477 | 107963.6251 | 107963.6251 | 0.1147
Solution 1 | stage0 | HEX pump ETS | hub14 | HEX pump ETS Mode 2 | 113.8479 | 56222.2696 | 56222.2696 | 0.056374
Solution 1 | stage0 | HEX pump ETS | hub2 | HEX pump ETS Mode 1 | 202.6796 | 68563.5179 | 68563.5179 | 0.038617
Solution 1 | stage0 | HEX pump ETS | hub2 | HEX pump ETS Mode 2 | 358.8817 | 250673.8742 | 250673.8742 | 0.079736
Solution 1 | stage0 | HEX pump ETS | hub3 | HEX pump ETS Mode 1 | 40.274 | 35618.2025 | 35618.2025 | 0.10096
Solution 1 | stage0 | HEX pump ETS | hub3 | HEX pump ETS Mode 2 | 110.3053 | 144478.019 | 144478.019 | 0.14952
Solution 1 | stage0 | HEX pump ETS | hub4 | HEX pump ETS Mode 1 | 185.8581 | 279910.2334 | 279910.2334 | 0.17192
Solution 1 | stage0 | HEX pump ETS | hub4 | HEX pump ETS Mode 2 | 632.3115 | 704151.5116 | 704151.5116 | 0.12713
Solution 1 | stage0 | HEX pump ETS | hub5 | HEX pump ETS Mode 1 | 89.2241 | 134681.4444 | 134681.4444 | 0.17231
Solution 1 | stage0 | HEX pump ETS | hub5 | HEX pump ETS Mode 2 | 333.1024 | 357408.3431 | 357408.3431 | 0.12249
Solution 1 | stage0 | HEX pump ETS | hub6 | HEX pump ETS Mode 1 | 83.8601 | 52608.8566 | 52608.8566 | 0.071614
Solution 1 | stage0 | HEX pump ETS | hub6 | HEX pump ETS Mode 2 | 140.3785 | 37131.4136 | 37131.4136 | 0.030195
Solution 1 | stage0 | HEX pump ETS | hub7 | HEX pump ETS Mode 1 | 68.8388 | 114191.9287 | 114191.9287 | 0.18936
Solution 1 | stage0 | HEX pump ETS | hub7 | HEX pump ETS Mode 2 | 227.7065 | 236394.7293 | 236394.7293 | 0.11851
Solution 1 | stage0 | HEX pump ETS | hub8 | HEX pump ETS Mode 1 | 65.8765 | 103531.2546 | 103531.2546 | 0.17941
Solution 1 | stage0 | HEX pump ETS | hub8 | HEX pump ETS Mode 2 | 234.5139 | 246006.1204 | 246006.1204 | 0.11975
Solution 1 | stage0 | HEX pump ETS | hub9 | HEX pump ETS Mode 1 | 463.8445 | 478355.0326 | 478355.0326 | 0.11773
Solution 1 | stage0 | HEX pump ETS | hub9 | HEX pump ETS Mode 2 | 1068.0941 | 1659907.0703 | 1659907.0703 | 0.17741
Solution 1 | stage0 | Main HP | plant | Main HP Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Main HP | plant | Main HP Mode 2 | 1158.4775 | 6406901.0981 | 6406901.0981 | 0.63133
Solution 1 | stage0 | Pump cooling | hub1 | Pump cooling Mode 1 | 2746.524 | 2915759.2445 | 2915759.2445 | 0.12119
Solution 1 | stage0 | Pump cooling | hub10 | Pump cooling Mode 1 | 43.5653 | 40007.4138 | 40007.4138 | 0.10483
Solution 1 | stage0 | Pump cooling | hub11 | Pump cooling Mode 1 | 266.7618 | 591625.2592 | 591625.2592 | 0.25317
Solution 1 | stage0 | Pump cooling | hub12 | Pump cooling Mode 1 | 4679.9342 | 9316324.8382 | 9316324.8382 | 0.22725
Solution 1 | stage0 | Pump cooling | hub13 | Pump cooling Mode 1 | 151.9881 | 69307.0831 | 69307.0831 | 0.052055
Solution 1 | stage0 | Pump cooling | hub14 | Pump cooling Mode 1 | 103.6616 | 51168.1813 | 51168.1813 | 0.056348
Solution 1 | stage0 | Pump cooling | hub2 | Pump cooling Mode 1 | 326.6423 | 228166.8433 | 228166.8433 | 0.07974
Solution 1 | stage0 | Pump cooling | hub3 | Pump cooling Mode 1 | 100.4378 | 131510.3058 | 131510.3058 | 0.14947
Solution 1 | stage0 | Pump cooling | hub4 | Pump cooling Mode 1 | 748.031 | 811707.9698 | 811707.9698 | 0.12387
Solution 1 | stage0 | Pump cooling | hub5 | Pump cooling Mode 1 | 380.9923 | 422265.8725 | 422265.8725 | 0.12652
Solution 1 | stage0 | Pump cooling | hub6 | Pump cooling Mode 1 | 127.8045 | 33799.1385 | 33799.1385 | 0.03019
Solution 1 | stage0 | Pump cooling | hub7 | Pump cooling Mode 1 | 264.3832 | 292396.6081 | 292396.6081 | 0.12625
Solution 1 | stage0 | Pump cooling | hub8 | Pump cooling Mode 1 | 267.1967 | 309788.5739 | 309788.5739 | 0.13235
Solution 1 | stage0 | Pump cooling | hub9 | Pump cooling Mode 1 | 1086.2268 | 1693852.2016 | 1693852.2016 | 0.17801
Solution 1 | stage0 | Pump DHW | hub1 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Pump DHW | hub10 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Pump DHW | hub11 | Pump DHW Mode 1 | 34.8297 | 157809.6407 | 157809.6407 | 0.51722
Solution 1 | stage0 | Pump DHW | hub12 | Pump DHW Mode 1 | 554.1475 | 3432869.3219 | 3432869.3219 | 0.70718
Solution 1 | stage0 | Pump DHW | hub13 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Pump DHW | hub14 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Pump DHW | hub2 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Pump DHW | hub3 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Pump DHW | hub4 | Pump DHW Mode 1 | 94.6748 | 355179.8886 | 355179.8886 | 0.42826
Solution 1 | stage0 | Pump DHW | hub5 | Pump DHW Mode 1 | 55.1879 | 207042.1928 | 207042.1928 | 0.42826
Solution 1 | stage0 | Pump DHW | hub6 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Pump DHW | hub7 | Pump DHW Mode 1 | 43.6957 | 163928.5463 | 163928.5463 | 0.42826
Solution 1 | stage0 | Pump DHW | hub8 | Pump DHW Mode 1 | 43.6957 | 163928.5463 | 163928.5463 | 0.42826
Solution 1 | stage0 | Pump DHW | hub9 | Pump DHW Mode 1 | 71.4402 | 268013.7936 | 268013.7936 | 0.42826
Solution 1 | stage0 | Pump SH | hub1 | Pump SH Mode 1 | 2304.5377 | 769002.1132 | 769002.1132 | 0.038093
Solution 1 | stage0 | Pump SH | hub10 | Pump SH Mode 1 | 135.9123 | 51886.8029 | 51886.8029 | 0.043581
Solution 1 | stage0 | Pump SH | hub11 | Pump SH Mode 1 | 218.5355 | 358030.5729 | 358030.5729 | 0.18702
Solution 1 | stage0 | Pump SH | hub12 | Pump SH Mode 1 | 2153.8699 | 7345736.8521 | 7345736.8521 | 0.38932
Solution 1 | stage0 | Pump SH | hub13 | Pump SH Mode 1 | 140.401 | 72255.5737 | 72255.5737 | 0.058749
Solution 1 | stage0 | Pump SH | hub14 | Pump SH Mode 1 | 142.1925 | 133678.2323 | 133678.2323 | 0.10732
Solution 1 | stage0 | Pump SH | hub2 | Pump SH Mode 1 | 279.8181 | 85065.6119 | 85065.6119 | 0.034704
Solution 1 | stage0 | Pump SH | hub3 | Pump SH Mode 1 | 58.7399 | 44423.8362 | 44423.8362 | 0.086333
Solution 1 | stage0 | Pump SH | hub4 | Pump SH Mode 1 | 273.5294 | 263452.5885 | 263452.5885 | 0.10995
Solution 1 | stage0 | Pump SH | hub5 | Pump SH Mode 1 | 136.167 | 116315.6148 | 116315.6148 | 0.097513
Solution 1 | stage0 | Pump SH | hub6 | Pump SH Mode 1 | 115.1239 | 65178.3221 | 65178.3221 | 0.06463
Solution 1 | stage0 | Pump SH | hub7 | Pump SH Mode 1 | 104.0534 | 100816.5425 | 100816.5425 | 0.1106
Solution 1 | stage0 | Pump SH | hub8 | Pump SH Mode 1 | 100.9653 | 97713.9952 | 97713.9952 | 0.11048
Solution 1 | stage0 | Pump SH | hub9 | Pump SH Mode 1 | 674.3585 | 577006.576 | 577006.576 | 0.097675
Solution 1 | stage0 | HEX SC ets | hub1 | HEX SC ets Mode 1 | 8.8973 | 768911.123 | 768.9111 | 0.0098657
Solution 1 | stage0 | HEX SC ets | hub10 | HEX SC ets Mode 1 | 0.30656 | 83904.426 | 83.9044 | 0.031199
Solution 1 | stage0 | HEX SC ets | hub11 | HEX SC ets Mode 1 | 0.61341 | 503110.5292 | 503.1105 | 0.093691
Solution 1 | stage0 | HEX SC ets | hub12 | HEX SC ets Mode 1 | 3.8336 | 10889135.3074 | 10889.1353 | 0.32422
Solution 1 | stage0 | HEX SC ets | hub13 | HEX SC ets Mode 1 | 0.49702 | 122683.2402 | 122.6832 | 0.028179
Solution 1 | stage0 | HEX SC ets | hub14 | HEX SC ets Mode 1 | 0.4369 | 216149.2536 | 216.1493 | 0.056464
Solution 1 | stage0 | HEX SC ets | hub2 | HEX SC ets Mode 1 | 1.1052 | 140115.1011 | 140.1151 | 0.014475
Solution 1 | stage0 | HEX SC ets | hub3 | HEX SC ets Mode 1 | 0.29564 | 79114.0515 | 79.1141 | 0.030511
Solution 1 | stage0 | HEX SC ets | hub4 | HEX SC ets Mode 1 | 1.4197 | 603381.1777 | 603.3812 | 0.048506
Solution 1 | stage0 | HEX SC ets | hub5 | HEX SC ets Mode 1 | 0.79459 | 293684.0729 | 293.6841 | 0.042171
Solution 1 | stage0 | HEX SC ets | hub6 | HEX SC ets Mode 1 | 0.44146 | 106312.6657 | 106.3127 | 0.02752
Solution 1 | stage0 | HEX SC ets | hub7 | HEX SC ets Mode 1 | 0.58171 | 246749.7364 | 246.7497 | 0.048398
Solution 1 | stage0 | HEX SC ets | hub8 | HEX SC ets Mode 1 | 0.58905 | 227692.3005 | 227.6923 | 0.044129
Solution 1 | stage0 | HEX SC ets | hub9 | HEX SC ets Mode 1 | 3.0105 | 965495.3393 | 965.4953 | 0.036617
Solution 1 | stage0 | ETS HP | hub1 | ETS HP Mode 1 | 2304.5377 | 147885.0218 | 769002.1132 | 0.038093
Solution 1 | stage0 | ETS HP | hub1 | ETS HP Mode 2 | 0.1 | 4.669 | 23.3449 | 0.026649
Solution 1 | stage0 | ETS HP | hub1 | ETS HP Mode 3 | 2942.64 | 191363.122 | 2870446.8297 | 0.11135
Solution 1 | stage0 | ETS HP | hub10 | ETS HP Mode 1 | 135.9123 | 9978.2313 | 51886.8029 | 0.043581
Solution 1 | stage0 | ETS HP | hub10 | ETS HP Mode 2 | 0.1 | 3.7817 | 18.9083 | 0.021585
Solution 1 | stage0 | ETS HP | hub10 | ETS HP Mode 3 | 46.6128 | 2859.9793 | 42899.6896 | 0.10506
Solution 1 | stage0 | ETS HP | hub11 | ETS HP Mode 1 | 218.5355 | 68852.0333 | 358030.5729 | 0.18702
Solution 1 | stage0 | ETS HP | hub11 | ETS HP Mode 2 | 62.7898 | 34448.6734 | 172243.3672 | 0.31315
Solution 1 | stage0 | ETS HP | hub11 | ETS HP Mode 3 | 245.4513 | 32189.7117 | 482845.6755 | 0.22456
Solution 1 | stage0 | ETS HP | hub12 | ETS HP Mode 1 | 2153.8699 | 1412641.7023 | 7345736.8521 | 0.38932
Solution 1 | stage0 | ETS HP | hub12 | ETS HP Mode 2 | 896.6397 | 732929.1686 | 3664645.8428 | 0.46656
Solution 1 | stage0 | ETS HP | hub12 | ETS HP Mode 3 | 4410.1151 | 473500.7026 | 7102510.5391 | 0.18385
Solution 1 | stage0 | ETS HP | hub13 | ETS HP Mode 1 | 140.401 | 13895.3026 | 72255.5737 | 0.058749
Solution 1 | stage0 | ETS HP | hub13 | ETS HP Mode 2 | 0.1 | 4.3505 | 21.7523 | 0.024831
Solution 1 | stage0 | ETS HP | hub13 | ETS HP Mode 3 | 162.7801 | 5162.5272 | 77437.9079 | 0.054306
Solution 1 | stage0 | ETS HP | hub14 | ETS HP Mode 1 | 142.1925 | 25707.3524 | 133678.2323 | 0.10732
Solution 1 | stage0 | ETS HP | hub14 | ETS HP Mode 2 | 0.1 | 2.0204 | 10.102 | 0.011532
Solution 1 | stage0 | ETS HP | hub14 | ETS HP Mode 3 | 111.0017 | 3661.8476 | 54927.7145 | 0.056488
Solution 1 | stage0 | ETS HP | hub2 | ETS HP Mode 1 | 279.8181 | 16358.7715 | 85065.6119 | 0.034704
Solution 1 | stage0 | ETS HP | hub2 | ETS HP Mode 2 | 0.1 | 3.2991 | 16.4957 | 0.018831
Solution 1 | stage0 | ETS HP | hub2 | ETS HP Mode 3 | 349.9096 | 16393.404 | 245901.06 | 0.080223
Solution 1 | stage0 | ETS HP | hub3 | ETS HP Mode 1 | 58.7399 | 8543.0454 | 44423.8362 | 0.086333
Solution 1 | stage0 | ETS HP | hub3 | ETS HP Mode 2 | 0.1 | 11.7695 | 58.8476 | 0.067178
Solution 1 | stage0 | ETS HP | hub3 | ETS HP Mode 3 | 107.5476 | 9653.6594 | 144804.8917 | 0.1537
Solution 1 | stage0 | ETS HP | hub4 | ETS HP Mode 1 | 273.5294 | 50663.9593 | 263452.5885 | 0.10995
Solution 1 | stage0 | ETS HP | hub4 | ETS HP Mode 2 | 287.7126 | 79834.5741 | 399172.8703 | 0.15838
Solution 1 | stage0 | ETS HP | hub4 | ETS HP Mode 3 | 616.5037 | 47221.872 | 708328.0793 | 0.13116
Solution 1 | stage0 | ETS HP | hub5 | ETS HP Mode 1 | 136.167 | 22368.3875 | 116315.6148 | 0.097513
Solution 1 | stage0 | ETS HP | hub5 | ETS HP Mode 2 | 129.782 | 46189.7345 | 230948.6723 | 0.20314
Solution 1 | stage0 | ETS HP | hub5 | ETS HP Mode 3 | 324.7748 | 24042.2484 | 360633.7266 | 0.12676
Solution 1 | stage0 | ETS HP | hub6 | ETS HP Mode 1 | 115.1239 | 12534.2927 | 65178.3221 | 0.06463
Solution 1 | stage0 | ETS HP | hub6 | ETS HP Mode 2 | 0.1 | 3.6259 | 18.1295 | 0.020696
Solution 1 | stage0 | ETS HP | hub6 | ETS HP Mode 3 | 136.8691 | 2450.0403 | 36750.6046 | 0.030652
Solution 1 | stage0 | ETS HP | hub7 | ETS HP Mode 1 | 104.0534 | 19387.7966 | 100816.5425 | 0.1106
Solution 1 | stage0 | ETS HP | hub7 | ETS HP Mode 2 | 95.2839 | 36884.2611 | 184421.3053 | 0.22095
Solution 1 | stage0 | ETS HP | hub7 | ETS HP Mode 3 | 222.0138 | 15977.8534 | 239667.8006 | 0.12323
Solution 1 | stage0 | ETS HP | hub8 | ETS HP Mode 1 | 100.9653 | 18791.1529 | 97713.9952 | 0.11048
Solution 1 | stage0 | ETS HP | hub8 | ETS HP Mode 2 | 89.6484 | 37073.0255 | 185365.1273 | 0.23604
Solution 1 | stage0 | ETS HP | hub8 | ETS HP Mode 3 | 228.651 | 16678.0575 | 250170.8631 | 0.1249
Solution 1 | stage0 | ETS HP | hub9 | ETS HP Mode 1 | 674.3585 | 110962.8031 | 577006.576 | 0.097675
Solution 1 | stage0 | ETS HP | hub9 | ETS HP Mode 2 | 190.4352 | 65313.6233 | 326568.1163 | 0.19576
Solution 1 | stage0 | ETS HP | hub9 | ETS HP Mode 3 | 1041.3918 | 108186.802 | 1622802.0306 | 0.17789
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub1 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub1 | Gas Boiler (Linearized cost) Mode 2 | 2.2204e-13 | -2.2397e-11 | -2.0157e-11 | 0
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub10 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub10 | Gas Boiler (Linearized cost) Mode 2 | 3.4694e-15 | -1.7615e-12 | -1.5854e-12 | 0
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub11 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub11 | Gas Boiler (Linearized cost) Mode 2 | 2.7756e-14 | -1.3512e-11 | -1.216e-11 | 0
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub12 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub12 | Gas Boiler (Linearized cost) Mode 2 | 4.4409e-13 | -2.8422e-10 | -2.558e-10 | 0
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub13 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub13 | Gas Boiler (Linearized cost) Mode 2 | 2.7756e-14 | -1.7238e-12 | -1.5514e-12 | 0
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub14 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub14 | Gas Boiler (Linearized cost) Mode 2 | 1.3878e-14 | -4.8481e-08 | -4.3633e-08 | 0
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub2 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub2 | Gas Boiler (Linearized cost) Mode 2 | 2.7756e-14 | -3.0027e-12 | -2.7024e-12 | 0
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub3 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub3 | Gas Boiler (Linearized cost) Mode 2 | 6.9389e-15 | -2.3916e-12 | -2.1524e-12 | 0
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub4 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub4 | Gas Boiler (Linearized cost) Mode 2 | 2.7756e-14 | -7.8289e-12 | -7.046e-12 | 0
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub5 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub5 | Gas Boiler (Linearized cost) Mode 2 | 1.3878e-14 | -4.184e-12 | -3.7656e-12 | 0
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub6 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub6 | Gas Boiler (Linearized cost) Mode 2 | 6.9389e-15 | -1.9171e-12 | -1.7254e-12 | 0
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub7 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub7 | Gas Boiler (Linearized cost) Mode 2 | 1.3878e-14 | -3.4385e-12 | -3.0947e-12 | 0
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub8 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub8 | Gas Boiler (Linearized cost) Mode 2 | 1.3878e-14 | -3.0405e-12 | -2.7364e-12 | 0
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub9 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 1 | stage0 | Gas Boiler (Linearized cost) | hub9 | Gas Boiler (Linearized cost) Mode 2 | 5.5511e-14 | -2.3405e-11 | -2.1065e-11 | 0
Solution 1 | stage0 | rooftop to pv | plant | rooftop to pv Mode 1 | 76.734 | 101314.917 | 101314.917 | 0.15072
Solution 2 | stage0 | parking to pv | plant | parking to pv Mode 1 | 0.1 | 132.034 | 132.034 | 0.15072
Solution 2 | stage0 | cooling tower plant | plant | cooling tower plant Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | cooling tower plant | plant | cooling tower plant Mode 2 | 1288.1478 | 7118728.2661 | 7118728.2661 | 0.63086
Solution 2 | stage0 | pv to hub | hub1 | pv to hub Mode 1 | 815.2307 | 631219.3732 | 631219.3732 | 0.088388
Solution 2 | stage0 | pv to hub | hub10 | pv to hub Mode 1 | 19.0762 | 35129.883 | 35129.883 | 0.21023
Solution 2 | stage0 | pv to hub | hub11 | pv to hub Mode 1 | 112.6625 | 265718.2244 | 265718.2244 | 0.26924
Solution 2 | stage0 | pv to hub | hub12 | pv to hub Mode 1 | 1539.7145 | 2512423.6844 | 2512423.6844 | 0.18627
Solution 2 | stage0 | pv to hub | hub13 | pv to hub Mode 1 | 14.2794 | 19333.9627 | 19333.9627 | 0.15457
Solution 2 | stage0 | pv to hub | hub14 | pv to hub Mode 1 | 12.1921 | 24839.5804 | 24839.5804 | 0.23258
Solution 2 | stage0 | pv to hub | hub2 | pv to hub Mode 1 | 73.8767 | 72295.944 | 72295.944 | 0.11171
Solution 2 | stage0 | pv to hub | hub3 | pv to hub Mode 1 | 62.3084 | 139531.2739 | 139531.2739 | 0.25564
Solution 2 | stage0 | pv to hub | hub4 | pv to hub Mode 1 | 143.4758 | 36378.7836 | 36378.7836 | 0.028944
Solution 2 | stage0 | pv to hub | hub5 | pv to hub Mode 1 | 79.0594 | 10901.6657 | 10901.6657 | 0.015741
Solution 2 | stage0 | pv to hub | hub6 | pv to hub Mode 1 | 71.9101 | 47964.0919 | 47964.0919 | 0.076142
Solution 2 | stage0 | pv to hub | hub7 | pv to hub Mode 1 | 57.1823 | 93121.4141 | 93121.4141 | 0.1859
Solution 2 | stage0 | pv to hub | hub8 | pv to hub Mode 1 | 60.1299 | 122272.5785 | 122272.5785 | 0.23213
Solution 2 | stage0 | pv to hub | hub9 | pv to hub Mode 1 | 330.3086 | 138690.196 | 138690.196 | 0.047932
Solution 2 | stage0 | pv to electricity | plant | pv to electricity Mode 1 | 321.6684 | 288544.7947 | 288544.7947 | 0.1024
Solution 2 | stage0 | Pump DHW gas | hub1 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Pump DHW gas | hub10 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Pump DHW gas | hub11 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Pump DHW gas | hub12 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Pump DHW gas | hub13 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Pump DHW gas | hub14 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Pump DHW gas | hub2 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Pump DHW gas | hub3 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Pump DHW gas | hub4 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Pump DHW gas | hub5 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Pump DHW gas | hub6 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Pump DHW gas | hub7 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Pump DHW gas | hub8 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Pump DHW gas | hub9 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | HEX pump ETS | hub1 | HEX pump ETS Mode 1 | 1506.007 | 381515.651 | 381515.651 | 0.028919
Solution 2 | stage0 | HEX pump ETS | hub1 | HEX pump ETS Mode 2 | 3018.0923 | 2941030.7286 | 2941030.7286 | 0.11124
Solution 2 | stage0 | HEX pump ETS | hub10 | HEX pump ETS Mode 1 | 106.6678 | 41908.9843 | 41908.9843 | 0.044851
Solution 2 | stage0 | HEX pump ETS | hub10 | HEX pump ETS Mode 2 | 47.808 | 43952.3271 | 43952.3271 | 0.10495
Solution 2 | stage0 | HEX pump ETS | hub11 | HEX pump ETS Mode 1 | 167.2098 | 247254.7095 | 247254.7095 | 0.1688
Solution 2 | stage0 | HEX pump ETS | hub11 | HEX pump ETS Mode 2 | 251.7449 | 490772.1483 | 490772.1483 | 0.22254
Solution 2 | stage0 | HEX pump ETS | hub12 | HEX pump ETS Mode 1 | 1916.8039 | 5454047.471 | 5454047.471 | 0.32482
Solution 2 | stage0 | HEX pump ETS | hub12 | HEX pump ETS Mode 2 | 4516.4882 | 7289709.2538 | 7289709.2538 | 0.18425
Solution 2 | stage0 | HEX pump ETS | hub13 | HEX pump ETS Mode 1 | 104.4963 | 58235.8836 | 58235.8836 | 0.063619
Solution 2 | stage0 | HEX pump ETS | hub13 | HEX pump ETS Mode 2 | 166.954 | 76149.0992 | 76149.0992 | 0.052067
Solution 2 | stage0 | HEX pump ETS | hub14 | HEX pump ETS Mode 1 | 107.4477 | 107965.5397 | 107965.5397 | 0.11471
Solution 2 | stage0 | HEX pump ETS | hub14 | HEX pump ETS Mode 2 | 113.8479 | 56222.73 | 56222.73 | 0.056374
Solution 2 | stage0 | HEX pump ETS | hub2 | HEX pump ETS Mode 1 | 202.6796 | 68565.2984 | 68565.2984 | 0.038618
Solution 2 | stage0 | HEX pump ETS | hub2 | HEX pump ETS Mode 2 | 358.8817 | 250674.9986 | 250674.9986 | 0.079736
Solution 2 | stage0 | HEX pump ETS | hub3 | HEX pump ETS Mode 1 | 40.274 | 35620.6064 | 35620.6064 | 0.10097
Solution 2 | stage0 | HEX pump ETS | hub3 | HEX pump ETS Mode 2 | 110.3053 | 144478.9002 | 144478.9002 | 0.14952
Solution 2 | stage0 | HEX pump ETS | hub4 | HEX pump ETS Mode 1 | 185.968 | 283627.9397 | 283627.9397 | 0.1741
Solution 2 | stage0 | HEX pump ETS | hub4 | HEX pump ETS Mode 2 | 657.868 | 706748.1803 | 706748.1803 | 0.12264
Solution 2 | stage0 | HEX pump ETS | hub5 | HEX pump ETS Mode 1 | 89.6684 | 136885.5619 | 136885.5619 | 0.17427
Solution 2 | stage0 | HEX pump ETS | hub5 | HEX pump ETS Mode 2 | 332.8322 | 358926.9544 | 358926.9544 | 0.12311
Solution 2 | stage0 | HEX pump ETS | hub6 | HEX pump ETS Mode 1 | 83.8601 | 52611.6329 | 52611.6329 | 0.071618
Solution 2 | stage0 | HEX pump ETS | hub6 | HEX pump ETS Mode 2 | 140.3785 | 37132.0911 | 37132.0911 | 0.030196
Solution 2 | stage0 | HEX pump ETS | hub7 | HEX pump ETS Mode 1 | 69.4998 | 115772.3768 | 115772.3768 | 0.19016
Solution 2 | stage0 | HEX pump ETS | hub7 | HEX pump ETS Mode 2 | 222.3941 | 238287.8554 | 238287.8554 | 0.12231
Solution 2 | stage0 | HEX pump ETS | hub8 | HEX pump ETS Mode 1 | 66.7487 | 105651.9546 | 105651.9546 | 0.18069
Solution 2 | stage0 | HEX pump ETS | hub8 | HEX pump ETS Mode 2 | 221.0959 | 248087.2358 | 248087.2358 | 0.12809
Solution 2 | stage0 | HEX pump ETS | hub9 | HEX pump ETS Mode 1 | 463.7871 | 480182.9206 | 480182.9206 | 0.11819
Solution 2 | stage0 | HEX pump ETS | hub9 | HEX pump ETS Mode 2 | 1068.9772 | 1667714.0674 | 1667714.0674 | 0.17809
Solution 2 | stage0 | Main HP | plant | Main HP Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Main HP | plant | Main HP Mode 2 | 1159.333 | 6406855.4395 | 6406855.4395 | 0.63086
Solution 2 | stage0 | Pump cooling | hub1 | Pump cooling Mode 1 | 2746.524 | 2915759.2445 | 2915759.2445 | 0.12119
Solution 2 | stage0 | Pump cooling | hub10 | Pump cooling Mode 1 | 43.5653 | 40007.4138 | 40007.4138 | 0.10483
Solution 2 | stage0 | Pump cooling | hub11 | Pump cooling Mode 1 | 266.7618 | 591625.2592 | 591625.2592 | 0.25317
Solution 2 | stage0 | Pump cooling | hub12 | Pump cooling Mode 1 | 4679.9342 | 9316324.8382 | 9316324.8382 | 0.22725
Solution 2 | stage0 | Pump cooling | hub13 | Pump cooling Mode 1 | 151.9881 | 69307.0831 | 69307.0831 | 0.052055
Solution 2 | stage0 | Pump cooling | hub14 | Pump cooling Mode 1 | 103.6616 | 51168.1813 | 51168.1813 | 0.056348
Solution 2 | stage0 | Pump cooling | hub2 | Pump cooling Mode 1 | 326.6423 | 228166.8433 | 228166.8433 | 0.07974
Solution 2 | stage0 | Pump cooling | hub3 | Pump cooling Mode 1 | 100.4378 | 131510.3058 | 131510.3058 | 0.14947
Solution 2 | stage0 | Pump cooling | hub4 | Pump cooling Mode 1 | 748.031 | 811707.9698 | 811707.9698 | 0.12387
Solution 2 | stage0 | Pump cooling | hub5 | Pump cooling Mode 1 | 380.9923 | 422265.8725 | 422265.8725 | 0.12652
Solution 2 | stage0 | Pump cooling | hub6 | Pump cooling Mode 1 | 127.8045 | 33799.1385 | 33799.1385 | 0.03019
Solution 2 | stage0 | Pump cooling | hub7 | Pump cooling Mode 1 | 264.3832 | 292396.6081 | 292396.6081 | 0.12625
Solution 2 | stage0 | Pump cooling | hub8 | Pump cooling Mode 1 | 267.1967 | 309788.5739 | 309788.5739 | 0.13235
Solution 2 | stage0 | Pump cooling | hub9 | Pump cooling Mode 1 | 1086.2268 | 1693852.2016 | 1693852.2016 | 0.17801
Solution 2 | stage0 | Pump DHW | hub1 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Pump DHW | hub10 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Pump DHW | hub11 | Pump DHW Mode 1 | 34.8297 | 157809.6407 | 157809.6407 | 0.51722
Solution 2 | stage0 | Pump DHW | hub12 | Pump DHW Mode 1 | 554.1475 | 3432869.3219 | 3432869.3219 | 0.70718
Solution 2 | stage0 | Pump DHW | hub13 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Pump DHW | hub14 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Pump DHW | hub2 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Pump DHW | hub3 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Pump DHW | hub4 | Pump DHW Mode 1 | 94.6748 | 355179.8886 | 355179.8886 | 0.42826
Solution 2 | stage0 | Pump DHW | hub5 | Pump DHW Mode 1 | 55.1879 | 207042.1928 | 207042.1928 | 0.42826
Solution 2 | stage0 | Pump DHW | hub6 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Pump DHW | hub7 | Pump DHW Mode 1 | 43.6957 | 163928.5463 | 163928.5463 | 0.42826
Solution 2 | stage0 | Pump DHW | hub8 | Pump DHW Mode 1 | 43.6957 | 163928.5463 | 163928.5463 | 0.42826
Solution 2 | stage0 | Pump DHW | hub9 | Pump DHW Mode 1 | 71.4402 | 268013.7936 | 268013.7936 | 0.42826
Solution 2 | stage0 | Pump SH | hub1 | Pump SH Mode 1 | 2304.5377 | 769002.1132 | 769002.1132 | 0.038093
Solution 2 | stage0 | Pump SH | hub10 | Pump SH Mode 1 | 135.9123 | 51886.8029 | 51886.8029 | 0.043581
Solution 2 | stage0 | Pump SH | hub11 | Pump SH Mode 1 | 218.5355 | 358030.5729 | 358030.5729 | 0.18702
Solution 2 | stage0 | Pump SH | hub12 | Pump SH Mode 1 | 2153.8699 | 7345736.8521 | 7345736.8521 | 0.38932
Solution 2 | stage0 | Pump SH | hub13 | Pump SH Mode 1 | 140.401 | 72255.5737 | 72255.5737 | 0.058749
Solution 2 | stage0 | Pump SH | hub14 | Pump SH Mode 1 | 142.1925 | 133678.2323 | 133678.2323 | 0.10732
Solution 2 | stage0 | Pump SH | hub2 | Pump SH Mode 1 | 279.8181 | 85065.6119 | 85065.6119 | 0.034704
Solution 2 | stage0 | Pump SH | hub3 | Pump SH Mode 1 | 58.7399 | 44423.8362 | 44423.8362 | 0.086333
Solution 2 | stage0 | Pump SH | hub4 | Pump SH Mode 1 | 273.5294 | 263452.5885 | 263452.5885 | 0.10995
Solution 2 | stage0 | Pump SH | hub5 | Pump SH Mode 1 | 136.167 | 116315.6148 | 116315.6148 | 0.097513
Solution 2 | stage0 | Pump SH | hub6 | Pump SH Mode 1 | 115.1239 | 65178.3221 | 65178.3221 | 0.06463
Solution 2 | stage0 | Pump SH | hub7 | Pump SH Mode 1 | 104.0534 | 100816.5425 | 100816.5425 | 0.1106
Solution 2 | stage0 | Pump SH | hub8 | Pump SH Mode 1 | 100.9653 | 97713.9952 | 97713.9952 | 0.11048
Solution 2 | stage0 | Pump SH | hub9 | Pump SH Mode 1 | 674.3585 | 577006.576 | 577006.576 | 0.097675
Solution 2 | stage0 | HEX SC ets | hub1 | HEX SC ets Mode 1 | 8.8973 | 768916.582 | 768.9166 | 0.0098658
Solution 2 | stage0 | HEX SC ets | hub10 | HEX SC ets Mode 1 | 0.30656 | 83911.1943 | 83.9112 | 0.031202
Solution 2 | stage0 | HEX SC ets | hub11 | HEX SC ets Mode 1 | 0.61341 | 503439.03 | 503.439 | 0.093752
Solution 2 | stage0 | HEX SC ets | hub12 | HEX SC ets Mode 1 | 3.8336 | 10908094.9421 | 10908.0949 | 0.32478
Solution 2 | stage0 | HEX SC ets | hub13 | HEX SC ets Mode 1 | 0.47613 | 120307.3634 | 120.3074 | 0.028852
Solution 2 | stage0 | HEX SC ets | hub14 | HEX SC ets Mode 1 | 0.4369 | 216153.0828 | 216.1531 | 0.056465
Solution 2 | stage0 | HEX SC ets | hub2 | HEX SC ets Mode 1 | 1.1052 | 140118.6621 | 140.1187 | 0.014475
Solution 2 | stage0 | HEX SC ets | hub3 | HEX SC ets Mode 1 | 0.29564 | 79118.8592 | 79.1189 | 0.030513
Solution 2 | stage0 | HEX SC ets | hub4 | HEX SC ets Mode 1 | 1.4166 | 610463.826 | 610.4638 | 0.04918
Solution 2 | stage0 | HEX SC ets | hub5 | HEX SC ets Mode 1 | 0.78215 | 296771.6551 | 296.7717 | 0.043322
Solution 2 | stage0 | HEX SC ets | hub6 | HEX SC ets Mode 1 | 0.44146 | 106318.2183 | 106.3182 | 0.027521
Solution 2 | stage0 | HEX SC ets | hub7 | HEX SC ets Mode 1 | 0.5632 | 247854.1085 | 247.8541 | 0.050256
Solution 2 | stage0 | HEX SC ets | hub8 | HEX SC ets Mode 1 | 0.56463 | 229336.9551 | 229.337 | 0.046336
Solution 2 | stage0 | HEX SC ets | hub9 | HEX SC ets Mode 1 | 3.0121 | 969164.8914 | 969.1649 | 0.036731
Solution 2 | stage0 | ETS HP | hub1 | ETS HP Mode 1 | 2304.5377 | 147885.0218 | 769002.1132 | 0.038093
Solution 2 | stage0 | ETS HP | hub1 | ETS HP Mode 2 | 0.10697 | 5.339 | 26.6951 | 0.030474
Solution 2 | stage0 | ETS HP | hub1 | ETS HP Mode 3 | 2942.64 | 191363.1734 | 2870447.6004 | 0.11135
Solution 2 | stage0 | ETS HP | hub10 | ETS HP Mode 1 | 135.9123 | 9978.2313 | 51886.8029 | 0.043581
Solution 2 | stage0 | ETS HP | hub10 | ETS HP Mode 2 | 0.1 | 4.7722 | 23.8608 | 0.027238
Solution 2 | stage0 | ETS HP | hub10 | ETS HP Mode 3 | 46.6128 | 2860.0088 | 42900.1317 | 0.10506
Solution 2 | stage0 | ETS HP | hub11 | ETS HP Mode 1 | 218.5355 | 68852.0333 | 358030.5729 | 0.18702
Solution 2 | stage0 | ETS HP | hub11 | ETS HP Mode 2 | 62.7898 | 34465.4759 | 172327.3797 | 0.3133
Solution 2 | stage0 | ETS HP | hub11 | ETS HP Mode 3 | 245.4513 | 32197.8433 | 482967.65 | 0.22462
Solution 2 | stage0 | ETS HP | hub12 | ETS HP Mode 1 | 2153.8699 | 1412641.7023 | 7345736.8521 | 0.38932
Solution 2 | stage0 | ETS HP | hub12 | ETS HP Mode 2 | 906.8117 | 734547.2462 | 3672736.2308 | 0.46235
Solution 2 | stage0 | ETS HP | hub12 | ETS HP Mode 3 | 4403.576 | 473831.1015 | 7107466.5225 | 0.18425
Solution 2 | stage0 | ETS HP | hub13 | ETS HP Mode 1 | 140.401 | 13895.3026 | 72255.5737 | 0.058749
Solution 2 | stage0 | ETS HP | hub13 | ETS HP Mode 2 | 0.1 | 4.9562 | 24.7809 | 0.028289
Solution 2 | stage0 | ETS HP | hub13 | ETS HP Mode 3 | 162.7801 | 5077.5447 | 76163.1699 | 0.053412
Solution 2 | stage0 | ETS HP | hub14 | ETS HP Mode 1 | 142.1925 | 25707.3524 | 133678.2323 | 0.10732
Solution 2 | stage0 | ETS HP | hub14 | ETS HP Mode 2 | 0.1003 | 2.5189 | 12.5947 | 0.014378
Solution 2 | stage0 | ETS HP | hub14 | ETS HP Mode 3 | 111.0017 | 3661.8776 | 54928.1635 | 0.056489
Solution 2 | stage0 | ETS HP | hub2 | ETS HP Mode 1 | 279.8181 | 16358.7715 | 85065.6119 | 0.034704
Solution 2 | stage0 | ETS HP | hub2 | ETS HP Mode 2 | 0.10002 | 3.5516 | 17.758 | 0.020272
Solution 2 | stage0 | ETS HP | hub2 | ETS HP Mode 3 | 349.9096 | 16393.4771 | 245902.1563 | 0.080224
Solution 2 | stage0 | ETS HP | hub3 | ETS HP Mode 1 | 58.7399 | 8543.0454 | 44423.8362 | 0.086333
Solution 2 | stage0 | ETS HP | hub3 | ETS HP Mode 2 | 0.10157 | 12.3035 | 61.5175 | 0.070225
Solution 2 | stage0 | ETS HP | hub3 | ETS HP Mode 3 | 107.5476 | 9653.7167 | 144805.7509 | 0.1537
Solution 2 | stage0 | ETS HP | hub4 | ETS HP Mode 1 | 273.5294 | 50663.9593 | 263452.5885 | 0.10995
Solution 2 | stage0 | ETS HP | hub4 | ETS HP Mode 2 | 248.9519 | 80282.2337 | 401411.1686 | 0.18406
Solution 2 | stage0 | ETS HP | hub4 | ETS HP Mode 3 | 641.4213 | 47378.8966 | 710683.4491 | 0.12648
Solution 2 | stage0 | ETS HP | hub5 | ETS HP Mode 1 | 136.167 | 22368.3875 | 116315.6148 | 0.097513
Solution 2 | stage0 | ETS HP | hub5 | ETS HP Mode 2 | 130.1918 | 46449.1209 | 232245.6047 | 0.20364
Solution 2 | stage0 | ETS HP | hub5 | ETS HP Mode 3 | 324.5114 | 24096.9364 | 361454.0463 | 0.12715
Solution 2 | stage0 | ETS HP | hub6 | ETS HP Mode 1 | 115.1239 | 12534.2927 | 65178.3221 | 0.06463
Solution 2 | stage0 | ETS HP | hub6 | ETS HP Mode 2 | 0.1 | 4.3458 | 21.7292 | 0.024805
Solution 2 | stage0 | ETS HP | hub6 | ETS HP Mode 3 | 136.8691 | 2450.0843 | 36751.2651 | 0.030652
Solution 2 | stage0 | ETS HP | hub7 | ETS HP Mode 1 | 104.0534 | 19387.7966 | 100816.5425 | 0.1106
Solution 2 | stage0 | ETS HP | hub7 | ETS HP Mode 2 | 103.341 | 36813.9786 | 184069.8929 | 0.20333
Solution 2 | stage0 | ETS HP | hub7 | ETS HP Mode 3 | 216.8342 | 16032.3558 | 240485.3365 | 0.12661
Solution 2 | stage0 | ETS HP | hub8 | ETS HP Mode 1 | 100.9653 | 18791.1529 | 97713.9952 | 0.11048
Solution 2 | stage0 | ETS HP | hub8 | ETS HP Mode 2 | 109.999 | 37119.8011 | 185599.0053 | 0.19261
Solution 2 | stage0 | ETS HP | hub8 | ETS HP Mode 3 | 215.5685 | 16726.7719 | 250901.5779 | 0.13287
Solution 2 | stage0 | ETS HP | hub9 | ETS HP Mode 1 | 674.3585 | 110962.8031 | 577006.576 | 0.097675
Solution 2 | stage0 | ETS HP | hub9 | ETS HP Mode 2 | 189.0959 | 63554.9499 | 317774.7493 | 0.19184
Solution 2 | stage0 | ETS HP | hub9 | ETS HP Mode 3 | 1042.2528 | 108694.7161 | 1630420.7408 | 0.17858
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub1 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub1 | Gas Boiler (Linearized cost) Mode 2 | 2.2204e-13 | -2.2397e-11 | -2.0157e-11 | 0
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub10 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub10 | Gas Boiler (Linearized cost) Mode 2 | 3.4694e-15 | -1.7615e-12 | -1.5854e-12 | 0
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub11 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub11 | Gas Boiler (Linearized cost) Mode 2 | 2.7756e-14 | -1.3512e-11 | -1.216e-11 | 0
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub12 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub12 | Gas Boiler (Linearized cost) Mode 2 | 4.4409e-13 | -2.8422e-10 | -2.558e-10 | 0
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub13 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub13 | Gas Boiler (Linearized cost) Mode 2 | 1.3878e-14 | -2.2172e-12 | -1.9955e-12 | 0
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub14 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub14 | Gas Boiler (Linearized cost) Mode 2 | 1.3878e-14 | -5.6267e-12 | -5.064e-12 | 0
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub2 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub2 | Gas Boiler (Linearized cost) Mode 2 | 2.7756e-14 | -3.0027e-12 | -2.7024e-12 | 0
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub3 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub3 | Gas Boiler (Linearized cost) Mode 2 | 6.9389e-15 | -2.4866e-12 | -2.238e-12 | 0
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub4 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub4 | Gas Boiler (Linearized cost) Mode 2 | 2.7756e-14 | -7.8906e-12 | -7.1015e-12 | 0
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub5 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub5 | Gas Boiler (Linearized cost) Mode 2 | 1.3878e-14 | -4.184e-12 | -3.7656e-12 | 0
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub6 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub6 | Gas Boiler (Linearized cost) Mode 2 | 6.9389e-15 | -2.3913e-12 | -2.1521e-12 | 0
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub7 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub7 | Gas Boiler (Linearized cost) Mode 2 | 1.3878e-14 | -3.4385e-12 | -3.0947e-12 | 0
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub8 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub8 | Gas Boiler (Linearized cost) Mode 2 | 1.3878e-14 | -3.0713e-12 | -2.7642e-12 | 0
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub9 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 2 | stage0 | Gas Boiler (Linearized cost) | hub9 | Gas Boiler (Linearized cost) Mode 2 | 5.5511e-14 | -2.3405e-11 | -2.1065e-11 | 0
Solution 2 | stage0 | rooftop to pv | plant | rooftop to pv Mode 1 | 3393.3764 | 4480410.8838 | 4480410.8838 | 0.15072
Solution 3 | stage0 | parking to pv | plant | parking to pv Mode 1 | 428.4382 | 565684.1953 | 565684.1953 | 0.15072
Solution 3 | stage0 | cooling tower plant | plant | cooling tower plant Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | cooling tower plant | plant | cooling tower plant Mode 2 | 1503.5918 | 7007857.6751 | 7007857.6751 | 0.53205
Solution 3 | stage0 | pv to hub | hub1 | pv to hub Mode 1 | 1124.7082 | 1319272.4018 | 1319272.4018 | 0.1339
Solution 3 | stage0 | pv to hub | hub10 | pv to hub Mode 1 | 25.7761 | 53273.23 | 53273.23 | 0.23593
Solution 3 | stage0 | pv to hub | hub11 | pv to hub Mode 1 | 137.8182 | 302439.2779 | 302439.2779 | 0.25051
Solution 3 | stage0 | pv to hub | hub12 | pv to hub Mode 1 | 1831.8778 | 4725576.2346 | 4725576.2346 | 0.29448
Solution 3 | stage0 | pv to hub | hub13 | pv to hub Mode 1 | 38.7899 | 59903.9319 | 59903.9319 | 0.17629
Solution 3 | stage0 | pv to hub | hub14 | pv to hub Mode 1 | 58.1681 | 78165.1388 | 78165.1388 | 0.1534
Solution 3 | stage0 | pv to hub | hub2 | pv to hub Mode 1 | 96.0606 | 164674.4894 | 164674.4894 | 0.19569
Solution 3 | stage0 | pv to hub | hub3 | pv to hub Mode 1 | 87.7564 | 197077.8458 | 197077.8458 | 0.25636
Solution 3 | stage0 | pv to hub | hub4 | pv to hub Mode 1 | 236.1856 | 194182.194 | 194182.194 | 0.093854
Solution 3 | stage0 | pv to hub | hub5 | pv to hub Mode 1 | 114.7826 | 107941.5296 | 107941.5296 | 0.10735
Solution 3 | stage0 | pv to hub | hub6 | pv to hub Mode 1 | 72.5934 | 55518.2903 | 55518.2903 | 0.087305
Solution 3 | stage0 | pv to hub | hub7 | pv to hub Mode 1 | 85.116 | 155979.3132 | 155979.3132 | 0.2092
Solution 3 | stage0 | pv to hub | hub8 | pv to hub Mode 1 | 86.4032 | 173515.6061 | 173515.6061 | 0.22925
Solution 3 | stage0 | pv to hub | hub9 | pv to hub Mode 1 | 485.2683 | 573061.7664 | 573061.7664 | 0.13481
Solution 3 | stage0 | pv to electricity | plant | pv to electricity Mode 1 | 421.0057 | 544411.2343 | 544411.2343 | 0.14762
Solution 3 | stage0 | Pump DHW gas | hub1 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Pump DHW gas | hub10 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Pump DHW gas | hub11 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Pump DHW gas | hub12 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Pump DHW gas | hub13 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Pump DHW gas | hub14 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Pump DHW gas | hub2 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Pump DHW gas | hub3 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Pump DHW gas | hub4 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Pump DHW gas | hub5 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Pump DHW gas | hub6 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Pump DHW gas | hub7 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Pump DHW gas | hub8 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Pump DHW gas | hub9 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | HEX pump ETS | hub1 | HEX pump ETS Mode 1 | 1506.007 | 381518.746 | 381518.746 | 0.028919
Solution 3 | stage0 | HEX pump ETS | hub1 | HEX pump ETS Mode 2 | 3018.0923 | 2941034.8181 | 2941034.8181 | 0.11124
Solution 3 | stage0 | HEX pump ETS | hub10 | HEX pump ETS Mode 1 | 106.6678 | 41913.1391 | 41913.1391 | 0.044855
Solution 3 | stage0 | HEX pump ETS | hub10 | HEX pump ETS Mode 2 | 47.808 | 43947.5687 | 43947.5687 | 0.10494
Solution 3 | stage0 | HEX pump ETS | hub11 | HEX pump ETS Mode 1 | 167.9563 | 249084.7232 | 249084.7232 | 0.1693
Solution 3 | stage0 | HEX pump ETS | hub11 | HEX pump ETS Mode 2 | 258.7418 | 492093.8743 | 492093.8743 | 0.21711
Solution 3 | stage0 | HEX pump ETS | hub12 | HEX pump ETS Mode 1 | 1922.0431 | 5446519.6739 | 5446519.6739 | 0.32348
Solution 3 | stage0 | HEX pump ETS | hub12 | HEX pump ETS Mode 2 | 4425.9129 | 7223241.5781 | 7223241.5781 | 0.18631
Solution 3 | stage0 | HEX pump ETS | hub13 | HEX pump ETS Mode 1 | 104.7669 | 58263.5745 | 58263.5745 | 0.063485
Solution 3 | stage0 | HEX pump ETS | hub13 | HEX pump ETS Mode 2 | 166.954 | 76151.9757 | 76151.9757 | 0.052069
Solution 3 | stage0 | HEX pump ETS | hub14 | HEX pump ETS Mode 1 | 107.4477 | 107968.6727 | 107968.6727 | 0.11471
Solution 3 | stage0 | HEX pump ETS | hub14 | HEX pump ETS Mode 2 | 113.8479 | 56218.904 | 56218.904 | 0.056371
Solution 3 | stage0 | HEX pump ETS | hub2 | HEX pump ETS Mode 1 | 202.6796 | 68571.8024 | 68571.8024 | 0.038622
Solution 3 | stage0 | HEX pump ETS | hub2 | HEX pump ETS Mode 2 | 358.8817 | 250647.4912 | 250647.4912 | 0.079727
Solution 3 | stage0 | HEX pump ETS | hub3 | HEX pump ETS Mode 1 | 40.274 | 35623.5905 | 35623.5905 | 0.10097
Solution 3 | stage0 | HEX pump ETS | hub3 | HEX pump ETS Mode 2 | 110.3053 | 144479.6641 | 144479.6641 | 0.14952
Solution 3 | stage0 | HEX pump ETS | hub4 | HEX pump ETS Mode 1 | 189.4114 | 285271.622 | 285271.622 | 0.17193
Solution 3 | stage0 | HEX pump ETS | hub4 | HEX pump ETS Mode 2 | 744.5013 | 714777.1979 | 714777.1979 | 0.1096
Solution 3 | stage0 | HEX pump ETS | hub5 | HEX pump ETS Mode 1 | 94.0818 | 139014.8559 | 139014.8559 | 0.16867
Solution 3 | stage0 | HEX pump ETS | hub5 | HEX pump ETS Mode 2 | 376.4978 | 364884.589 | 364884.589 | 0.11063
Solution 3 | stage0 | HEX pump ETS | hub6 | HEX pump ETS Mode 1 | 83.8601 | 52614.8718 | 52614.8718 | 0.071623
Solution 3 | stage0 | HEX pump ETS | hub6 | HEX pump ETS Mode 2 | 140.3785 | 37134.6477 | 37134.6477 | 0.030198
Solution 3 | stage0 | HEX pump ETS | hub7 | HEX pump ETS Mode 1 | 71.1854 | 117060.9762 | 117060.9762 | 0.18772
Solution 3 | stage0 | HEX pump ETS | hub7 | HEX pump ETS Mode 2 | 256.3135 | 242630.0955 | 242630.0955 | 0.10806
Solution 3 | stage0 | HEX pump ETS | hub8 | HEX pump ETS Mode 1 | 68.4318 | 106252.7555 | 106252.7555 | 0.17725
Solution 3 | stage0 | HEX pump ETS | hub8 | HEX pump ETS Mode 2 | 258.1311 | 252052.2497 | 252052.2497 | 0.11147
Solution 3 | stage0 | HEX pump ETS | hub9 | HEX pump ETS Mode 1 | 460.6506 | 481296.4324 | 481296.4324 | 0.11927
Solution 3 | stage0 | HEX pump ETS | hub9 | HEX pump ETS Mode 2 | 1117.2296 | 1674800.9765 | 1674800.9765 | 0.17113
Solution 3 | stage0 | Main HP | plant | Main HP Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Main HP | plant | Main HP Mode 2 | 1353.2326 | 6307071.9076 | 6307071.9076 | 0.53205
Solution 3 | stage0 | Pump cooling | hub1 | Pump cooling Mode 1 | 2746.524 | 2915759.2445 | 2915759.2445 | 0.12119
Solution 3 | stage0 | Pump cooling | hub10 | Pump cooling Mode 1 | 43.5653 | 40007.4138 | 40007.4138 | 0.10483
Solution 3 | stage0 | Pump cooling | hub11 | Pump cooling Mode 1 | 266.7618 | 591625.2592 | 591625.2592 | 0.25317
Solution 3 | stage0 | Pump cooling | hub12 | Pump cooling Mode 1 | 4679.9342 | 9316324.8382 | 9316324.8382 | 0.22725
Solution 3 | stage0 | Pump cooling | hub13 | Pump cooling Mode 1 | 151.9881 | 69307.0831 | 69307.0831 | 0.052055
Solution 3 | stage0 | Pump cooling | hub14 | Pump cooling Mode 1 | 103.6616 | 51168.1813 | 51168.1813 | 0.056348
Solution 3 | stage0 | Pump cooling | hub2 | Pump cooling Mode 1 | 326.6423 | 228166.8433 | 228166.8433 | 0.07974
Solution 3 | stage0 | Pump cooling | hub3 | Pump cooling Mode 1 | 100.4378 | 131510.3058 | 131510.3058 | 0.14947
Solution 3 | stage0 | Pump cooling | hub4 | Pump cooling Mode 1 | 748.031 | 811707.9698 | 811707.9698 | 0.12387
Solution 3 | stage0 | Pump cooling | hub5 | Pump cooling Mode 1 | 380.9923 | 422265.8725 | 422265.8725 | 0.12652
Solution 3 | stage0 | Pump cooling | hub6 | Pump cooling Mode 1 | 127.8045 | 33799.1385 | 33799.1385 | 0.03019
Solution 3 | stage0 | Pump cooling | hub7 | Pump cooling Mode 1 | 264.3832 | 292396.6081 | 292396.6081 | 0.12625
Solution 3 | stage0 | Pump cooling | hub8 | Pump cooling Mode 1 | 267.1967 | 309788.5739 | 309788.5739 | 0.13235
Solution 3 | stage0 | Pump cooling | hub9 | Pump cooling Mode 1 | 1086.2268 | 1693852.2016 | 1693852.2016 | 0.17801
Solution 3 | stage0 | Pump DHW | hub1 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Pump DHW | hub10 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Pump DHW | hub11 | Pump DHW Mode 1 | 34.8297 | 157809.6407 | 157809.6407 | 0.51722
Solution 3 | stage0 | Pump DHW | hub12 | Pump DHW Mode 1 | 554.1475 | 3432869.3219 | 3432869.3219 | 0.70718
Solution 3 | stage0 | Pump DHW | hub13 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Pump DHW | hub14 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Pump DHW | hub2 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Pump DHW | hub3 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Pump DHW | hub4 | Pump DHW Mode 1 | 94.6748 | 355179.8886 | 355179.8886 | 0.42826
Solution 3 | stage0 | Pump DHW | hub5 | Pump DHW Mode 1 | 55.1879 | 207042.1928 | 207042.1928 | 0.42826
Solution 3 | stage0 | Pump DHW | hub6 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Pump DHW | hub7 | Pump DHW Mode 1 | 43.6957 | 163928.5463 | 163928.5463 | 0.42826
Solution 3 | stage0 | Pump DHW | hub8 | Pump DHW Mode 1 | 43.6957 | 163928.5463 | 163928.5463 | 0.42826
Solution 3 | stage0 | Pump DHW | hub9 | Pump DHW Mode 1 | 71.4402 | 268013.7936 | 268013.7936 | 0.42826
Solution 3 | stage0 | Pump SH | hub1 | Pump SH Mode 1 | 2304.5377 | 769002.1132 | 769002.1132 | 0.038093
Solution 3 | stage0 | Pump SH | hub10 | Pump SH Mode 1 | 135.9123 | 51886.8029 | 51886.8029 | 0.043581
Solution 3 | stage0 | Pump SH | hub11 | Pump SH Mode 1 | 218.5355 | 358030.5729 | 358030.5729 | 0.18702
Solution 3 | stage0 | Pump SH | hub12 | Pump SH Mode 1 | 2153.8699 | 7345736.8521 | 7345736.8521 | 0.38932
Solution 3 | stage0 | Pump SH | hub13 | Pump SH Mode 1 | 140.401 | 72255.5737 | 72255.5737 | 0.058749
Solution 3 | stage0 | Pump SH | hub14 | Pump SH Mode 1 | 142.1925 | 133678.2323 | 133678.2323 | 0.10732
Solution 3 | stage0 | Pump SH | hub2 | Pump SH Mode 1 | 279.8181 | 85065.6119 | 85065.6119 | 0.034704
Solution 3 | stage0 | Pump SH | hub3 | Pump SH Mode 1 | 58.7399 | 44423.8362 | 44423.8362 | 0.086333
Solution 3 | stage0 | Pump SH | hub4 | Pump SH Mode 1 | 273.5294 | 263452.5885 | 263452.5885 | 0.10995
Solution 3 | stage0 | Pump SH | hub5 | Pump SH Mode 1 | 136.167 | 116315.6148 | 116315.6148 | 0.097513
Solution 3 | stage0 | Pump SH | hub6 | Pump SH Mode 1 | 115.1239 | 65178.3221 | 65178.3221 | 0.06463
Solution 3 | stage0 | Pump SH | hub7 | Pump SH Mode 1 | 104.0534 | 100816.5425 | 100816.5425 | 0.1106
Solution 3 | stage0 | Pump SH | hub8 | Pump SH Mode 1 | 100.9653 | 97713.9952 | 97713.9952 | 0.11048
Solution 3 | stage0 | Pump SH | hub9 | Pump SH Mode 1 | 674.3585 | 577006.576 | 577006.576 | 0.097675
Solution 3 | stage0 | HEX SC ets | hub1 | HEX SC ets Mode 1 | 8.8973 | 768922.7721 | 768.9228 | 0.0098659
Solution 3 | stage0 | HEX SC ets | hub10 | HEX SC ets Mode 1 | 0.30656 | 83919.5038 | 83.9195 | 0.031205
Solution 3 | stage0 | HEX SC ets | hub11 | HEX SC ets Mode 1 | 0.59251 | 505235.274 | 505.2353 | 0.09726
Solution 3 | stage0 | HEX SC ets | hub12 | HEX SC ets Mode 1 | 4.0488 | 10893244.078 | 10893.2441 | 0.30712
Solution 3 | stage0 | HEX SC ets | hub13 | HEX SC ets Mode 1 | 0.46855 | 119604.1349 | 119.6041 | 0.029112
Solution 3 | stage0 | HEX SC ets | hub14 | HEX SC ets Mode 1 | 0.4369 | 216159.3488 | 216.1593 | 0.056466
Solution 3 | stage0 | HEX SC ets | hub2 | HEX SC ets Mode 1 | 1.1052 | 140131.6702 | 140.1317 | 0.014477
Solution 3 | stage0 | HEX SC ets | hub3 | HEX SC ets Mode 1 | 0.29564 | 79124.8274 | 79.1248 | 0.030515
Solution 3 | stage0 | HEX SC ets | hub4 | HEX SC ets Mode 1 | 1.3202 | 605210.4918 | 605.2105 | 0.052339
Solution 3 | stage0 | HEX SC ets | hub5 | HEX SC ets Mode 1 | 0.65858 | 290323.6344 | 290.3236 | 0.050291
Solution 3 | stage0 | HEX SC ets | hub6 | HEX SC ets Mode 1 | 0.44146 | 106324.6963 | 106.3247 | 0.027523
Solution 3 | stage0 | HEX SC ets | hub7 | HEX SC ets Mode 1 | 0.516 | 246471.3605 | 246.4714 | 0.054527
Solution 3 | stage0 | HEX SC ets | hub8 | HEX SC ets Mode 1 | 0.51751 | 226364.4196 | 226.3644 | 0.049885
Solution 3 | stage0 | HEX SC ets | hub9 | HEX SC ets Mode 1 | 3.0999 | 972687.3231 | 972.6873 | 0.035819
Solution 3 | stage0 | ETS HP | hub1 | ETS HP Mode 1 | 2304.5377 | 147885.0218 | 769002.1132 | 0.038093
Solution 3 | stage0 | ETS HP | hub1 | ETS HP Mode 2 | 0.1 | 5.1302 | 25.651 | 0.029282
Solution 3 | stage0 | ETS HP | hub1 | ETS HP Mode 3 | 2942.64 | 191363.4392 | 2870451.5877 | 0.11135
Solution 3 | stage0 | ETS HP | hub10 | ETS HP Mode 1 | 135.9123 | 9978.2313 | 51886.8029 | 0.043581
Solution 3 | stage0 | ETS HP | hub10 | ETS HP Mode 2 | 0.1 | 7.6004 | 38.0022 | 0.043382
Solution 3 | stage0 | ETS HP | hub10 | ETS HP Mode 3 | 46.6128 | 2859.6995 | 42895.4923 | 0.10505
Solution 3 | stage0 | ETS HP | hub11 | ETS HP Mode 1 | 218.5355 | 68852.0333 | 358030.5729 | 0.18702
Solution 3 | stage0 | ETS HP | hub11 | ETS HP Mode 2 | 52.1779 | 34653.8482 | 173269.241 | 0.37908
Solution 3 | stage0 | ETS HP | hub11 | ETS HP Mode 3 | 252.2732 | 32221.6294 | 483324.4413 | 0.21871
Solution 3 | stage0 | ETS HP | hub12 | ETS HP Mode 1 | 2153.8699 | 1412641.7023 | 7345736.8521 | 0.38932
Solution 3 | stage0 | ETS HP | hub12 | ETS HP Mode 2 | 1044.1842 | 752202.1169 | 3761010.5844 | 0.41117
Solution 3 | stage0 | ETS HP | hub12 | ETS HP Mode 3 | 4315.2651 | 469517.5269 | 7042762.9037 | 0.18631
Solution 3 | stage0 | ETS HP | hub13 | ETS HP Mode 1 | 140.401 | 13895.3026 | 72255.5737 | 0.058749
Solution 3 | stage0 | ETS HP | hub13 | ETS HP Mode 2 | 0.1 | 4.8849 | 24.4247 | 0.027882
Solution 3 | stage0 | ETS HP | hub13 | ETS HP Mode 3 | 162.7801 | 5052.4446 | 75786.6693 | 0.053148
Solution 3 | stage0 | ETS HP | hub14 | ETS HP Mode 1 | 142.1925 | 25707.3524 | 133678.2323 | 0.10732
Solution 3 | stage0 | ETS HP | hub14 | ETS HP Mode 2 | 0.1 | 4.7238 | 23.6191 | 0.026962
Solution 3 | stage0 | ETS HP | hub14 | ETS HP Mode 3 | 111.0017 | 3661.6289 | 54924.4331 | 0.056485
Solution 3 | stage0 | ETS HP | hub2 | ETS HP Mode 1 | 279.8181 | 16358.7715 | 85065.6119 | 0.034704
Solution 3 | stage0 | ETS HP | hub2 | ETS HP Mode 2 | 0.1004 | 14.0635 | 70.3174 | 0.080271
Solution 3 | stage0 | ETS HP | hub2 | ETS HP Mode 3 | 349.9096 | 16391.6891 | 245875.3366 | 0.080215
Solution 3 | stage0 | ETS HP | hub3 | ETS HP Mode 1 | 58.7399 | 8543.0454 | 44423.8362 | 0.086333
Solution 3 | stage0 | ETS HP | hub3 | ETS HP Mode 2 | 0.1 | 13.0665 | 65.3325 | 0.07458
Solution 3 | stage0 | ETS HP | hub3 | ETS HP Mode 3 | 107.5476 | 9653.7664 | 144806.4957 | 0.1537
Solution 3 | stage0 | ETS HP | hub4 | ETS HP Mode 1 | 273.5294 | 50663.9593 | 263452.5885 | 0.10995
Solution 3 | stage0 | ETS HP | hub4 | ETS HP Mode 2 | 117.558 | 78299.7625 | 391498.8124 | 0.38017
Solution 3 | stage0 | ETS HP | hub4 | ETS HP Mode 3 | 725.8888 | 47616.0928 | 714241.3919 | 0.11232
Solution 3 | stage0 | ETS HP | hub5 | ETS HP Mode 1 | 136.167 | 22368.3875 | 116315.6148 | 0.097513
Solution 3 | stage0 | ETS HP | hub5 | ETS HP Mode 2 | 63.9656 | 45232.7741 | 226163.8707 | 0.40362
Solution 3 | stage0 | ETS HP | hub5 | ETS HP Mode 3 | 367.0853 | 24127.2957 | 361909.4356 | 0.11255
Solution 3 | stage0 | ETS HP | hub6 | ETS HP Mode 1 | 115.1239 | 12534.2927 | 65178.3221 | 0.06463
Solution 3 | stage0 | ETS HP | hub6 | ETS HP Mode 2 | 0.1 | 4.65 | 23.2499 | 0.026541
Solution 3 | stage0 | ETS HP | hub6 | ETS HP Mode 3 | 136.8691 | 2450.2505 | 36753.7578 | 0.030654
Solution 3 | stage0 | ETS HP | hub7 | ETS HP Mode 1 | 104.0534 | 19387.7966 | 100816.5425 | 0.1106
Solution 3 | stage0 | ETS HP | hub7 | ETS HP Mode 2 | 51.8966 | 35882.3662 | 179411.8308 | 0.39464
Solution 3 | stage0 | ETS HP | hub7 | ETS HP Mode 3 | 249.9056 | 16182.6031 | 242739.0471 | 0.11088
Solution 3 | stage0 | ETS HP | hub8 | ETS HP Mode 1 | 100.9653 | 18791.1529 | 97713.9952 | 0.11048
Solution 3 | stage0 | ETS HP | hub8 | ETS HP Mode 2 | 53.8289 | 36070.9679 | 180354.8394 | 0.38248
Solution 3 | stage0 | ETS HP | hub8 | ETS HP Mode 3 | 251.6779 | 16845.3598 | 252680.3977 | 0.11461
Solution 3 | stage0 | ETS HP | hub9 | ETS HP Mode 1 | 674.3585 | 110962.8031 | 577006.576 | 0.097675
Solution 3 | stage0 | ETS HP | hub9 | ETS HP Mode 2 | 115.913 | 61790.8181 | 308954.0907 | 0.30427
Solution 3 | stage0 | ETS HP | hub9 | ETS HP Mode 3 | 1089.2989 | 109198.5454 | 1637978.1812 | 0.17166
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub1 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub1 | Gas Boiler (Linearized cost) Mode 2 | 2.2204e-13 | -2.8399e-11 | -2.5559e-11 | 0
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub10 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub10 | Gas Boiler (Linearized cost) Mode 2 | 3.4694e-15 | -1.7615e-12 | -1.5854e-12 | 0
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub11 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub11 | Gas Boiler (Linearized cost) Mode 2 | 2.7756e-14 | -2.2719e-11 | -2.0447e-11 | 0
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub12 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub12 | Gas Boiler (Linearized cost) Mode 2 | 4.4409e-13 | -2.9902e-10 | -2.6912e-10 | 0
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub13 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub13 | Gas Boiler (Linearized cost) Mode 2 | 1.3878e-14 | -9.4298e-12 | -8.4869e-12 | 0
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub14 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub14 | Gas Boiler (Linearized cost) Mode 2 | 1.3878e-14 | -5.6267e-12 | -5.064e-12 | 0
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub2 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub2 | Gas Boiler (Linearized cost) Mode 2 | 2.7756e-14 | -3.0027e-12 | -2.7024e-12 | 0
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub3 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub3 | Gas Boiler (Linearized cost) Mode 2 | 6.9389e-15 | -3.5654e-12 | -3.2089e-12 | 0
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub4 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub4 | Gas Boiler (Linearized cost) Mode 2 | 2.7756e-14 | -2.2433e-11 | -2.019e-11 | 0
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub5 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub5 | Gas Boiler (Linearized cost) Mode 2 | 1.3878e-14 | -4.2456e-12 | -3.8211e-12 | 0
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub6 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub6 | Gas Boiler (Linearized cost) Mode 2 | 6.9389e-15 | -7.0586e-12 | -6.3528e-12 | 0
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub7 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub7 | Gas Boiler (Linearized cost) Mode 2 | 1.3878e-14 | -3.6544e-12 | -3.289e-12 | 0
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub8 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub8 | Gas Boiler (Linearized cost) Mode 2 | 1.3878e-14 | -9.137e-12 | -8.2233e-12 | 0
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub9 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 3 | stage0 | Gas Boiler (Linearized cost) | hub9 | Gas Boiler (Linearized cost) Mode 2 | 5.5511e-14 | -3.7457e-11 | -3.3712e-11 | 0
Solution 3 | stage0 | rooftop to pv | plant | rooftop to pv Mode 1 | 6584.7276 | 8694079.8505 | 8694079.8505 | 0.15072
Solution 4 | stage0 | parking to pv | plant | parking to pv Mode 1 | 5043.6508 | 6659334.3125 | 6659334.3125 | 0.15072
Solution 4 | stage0 | cooling tower plant | plant | cooling tower plant Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | cooling tower plant | plant | cooling tower plant Mode 2 | 4024.8833 | 6746273.8336 | 6746273.8336 | 0.19134
Solution 4 | stage0 | pv to hub | hub1 | pv to hub Mode 1 | 1584.2629 | 2193624.3508 | 2193624.3508 | 0.15806
Solution 4 | stage0 | pv to hub | hub10 | pv to hub Mode 1 | 35.0766 | 46988.1648 | 46988.1648 | 0.15292
Solution 4 | stage0 | pv to hub | hub11 | pv to hub Mode 1 | 191.9448 | 363842.508 | 363842.508 | 0.21639
Solution 4 | stage0 | pv to hub | hub12 | pv to hub Mode 1 | 2281.6613 | 5855528.6572 | 5855528.6572 | 0.29296
Solution 4 | stage0 | pv to hub | hub13 | pv to hub Mode 1 | 66.6593 | 57290.6716 | 57290.6716 | 0.098112
Solution 4 | stage0 | pv to hub | hub14 | pv to hub Mode 1 | 60.4908 | 71551.0898 | 71551.0898 | 0.13503
Solution 4 | stage0 | pv to hub | hub2 | pv to hub Mode 1 | 143.7961 | 224963.5681 | 224963.5681 | 0.17859
Solution 4 | stage0 | pv to hub | hub3 | pv to hub Mode 1 | 90.3808 | 262356.8504 | 262356.8504 | 0.33137
Solution 4 | stage0 | pv to hub | hub4 | pv to hub Mode 1 | 308.8689 | 573718.9812 | 573718.9812 | 0.21204
Solution 4 | stage0 | pv to hub | hub5 | pv to hub Mode 1 | 155.8117 | 303602.0522 | 303602.0522 | 0.22243
Solution 4 | stage0 | pv to hub | hub6 | pv to hub Mode 1 | 73.2644 | 54802.3883 | 54802.3883 | 0.08539
Solution 4 | stage0 | pv to hub | hub7 | pv to hub Mode 1 | 115.5563 | 202809.2374 | 202809.2374 | 0.20035
Solution 4 | stage0 | pv to hub | hub8 | pv to hub Mode 1 | 104.0852 | 201105.3735 | 201105.3735 | 0.22056
Solution 4 | stage0 | pv to hub | hub9 | pv to hub Mode 1 | 774.5333 | 1399484.2301 | 1399484.2301 | 0.20626
Solution 4 | stage0 | pv to electricity | plant | pv to electricity Mode 1 | 1126.9673 | 1388038.006 | 1388038.006 | 0.1406
Solution 4 | stage0 | Pump DHW gas | hub1 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Pump DHW gas | hub10 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Pump DHW gas | hub11 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Pump DHW gas | hub12 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Pump DHW gas | hub13 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Pump DHW gas | hub14 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Pump DHW gas | hub2 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Pump DHW gas | hub3 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Pump DHW gas | hub4 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Pump DHW gas | hub5 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Pump DHW gas | hub6 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Pump DHW gas | hub7 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Pump DHW gas | hub8 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Pump DHW gas | hub9 | Pump DHW gas Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | HEX pump ETS | hub1 | HEX pump ETS Mode 1 | 1506.007 | 381543.7573 | 381543.7573 | 0.028921
Solution 4 | stage0 | HEX pump ETS | hub1 | HEX pump ETS Mode 2 | 3018.0923 | 2940980.063 | 2940980.063 | 0.11124
Solution 4 | stage0 | HEX pump ETS | hub10 | HEX pump ETS Mode 1 | 106.6678 | 41946.3442 | 41946.3442 | 0.044891
Solution 4 | stage0 | HEX pump ETS | hub10 | HEX pump ETS Mode 2 | 47.808 | 43911.6227 | 43911.6227 | 0.10485
Solution 4 | stage0 | HEX pump ETS | hub11 | HEX pump ETS Mode 1 | 176.5094 | 259895.5967 | 259895.5967 | 0.16808
Solution 4 | stage0 | HEX pump ETS | hub11 | HEX pump ETS Mode 2 | 243.3439 | 480815.1168 | 480815.1168 | 0.22556
Solution 4 | stage0 | HEX pump ETS | hub12 | HEX pump ETS Mode 1 | 2748.1068 | 5601521.4937 | 5601521.4937 | 0.23268
Solution 4 | stage0 | HEX pump ETS | hub12 | HEX pump ETS Mode 2 | 4352.5634 | 7150365.2362 | 7150365.2362 | 0.18753
Solution 4 | stage0 | HEX pump ETS | hub13 | HEX pump ETS Mode 1 | 108.0765 | 58398.5824 | 58398.5824 | 0.061683
Solution 4 | stage0 | HEX pump ETS | hub13 | HEX pump ETS Mode 2 | 166.954 | 76110.7545 | 76110.7545 | 0.052041
Solution 4 | stage0 | HEX pump ETS | hub14 | HEX pump ETS Mode 1 | 107.4477 | 108007.9577 | 108007.9577 | 0.11475
Solution 4 | stage0 | HEX pump ETS | hub14 | HEX pump ETS Mode 2 | 113.8479 | 56180.6304 | 56180.6304 | 0.056332
Solution 4 | stage0 | HEX pump ETS | hub2 | HEX pump ETS Mode 1 | 226.0069 | 68682.0551 | 68682.0551 | 0.034691
Solution 4 | stage0 | HEX pump ETS | hub2 | HEX pump ETS Mode 2 | 358.8817 | 250606.1699 | 250606.1699 | 0.079714
Solution 4 | stage0 | HEX pump ETS | hub3 | HEX pump ETS Mode 1 | 47.2552 | 35899.031 | 35899.031 | 0.086722
Solution 4 | stage0 | HEX pump ETS | hub3 | HEX pump ETS Mode 2 | 110.3053 | 144439.0321 | 144439.0321 | 0.14948
Solution 4 | stage0 | HEX pump ETS | hub4 | HEX pump ETS Mode 1 | 220.7909 | 317479.2486 | 317479.2486 | 0.16415
Solution 4 | stage0 | HEX pump ETS | hub4 | HEX pump ETS Mode 2 | 664.1812 | 722702.7197 | 722702.7197 | 0.12421
Solution 4 | stage0 | HEX pump ETS | hub5 | HEX pump ETS Mode 1 | 109.7622 | 160768.5398 | 160768.5398 | 0.1672
Solution 4 | stage0 | HEX pump ETS | hub5 | HEX pump ETS Mode 2 | 326.6641 | 372366.3283 | 372366.3283 | 0.13013
Solution 4 | stage0 | HEX pump ETS | hub6 | HEX pump ETS Mode 1 | 92.9847 | 52697.6839 | 52697.6839 | 0.064696
Solution 4 | stage0 | HEX pump ETS | hub6 | HEX pump ETS Mode 2 | 140.3785 | 37105.7923 | 37105.7923 | 0.030174
Solution 4 | stage0 | HEX pump ETS | hub7 | HEX pump ETS Mode 1 | 83.6398 | 132571.4193 | 132571.4193 | 0.18094
Solution 4 | stage0 | HEX pump ETS | hub7 | HEX pump ETS Mode 2 | 217.7629 | 247064.0357 | 247064.0357 | 0.12952
Solution 4 | stage0 | HEX pump ETS | hub8 | HEX pump ETS Mode 1 | 82.0974 | 121343.976 | 121343.976 | 0.16873
Solution 4 | stage0 | HEX pump ETS | hub8 | HEX pump ETS Mode 2 | 220.8546 | 256558.6253 | 256558.6253 | 0.13261
Solution 4 | stage0 | HEX pump ETS | hub9 | HEX pump ETS Mode 1 | 513.6232 | 494398.4901 | 494398.4901 | 0.10988
Solution 4 | stage0 | HEX pump ETS | hub9 | HEX pump ETS Mode 2 | 1074.6115 | 1675157.4824 | 1675157.4824 | 0.17795
Solution 4 | stage0 | Main HP | plant | Main HP Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Main HP | plant | Main HP Mode 2 | 3622.395 | 6071646.4503 | 6071646.4503 | 0.19134
Solution 4 | stage0 | Pump cooling | hub1 | Pump cooling Mode 1 | 2746.524 | 2915759.2445 | 2915759.2445 | 0.12119
Solution 4 | stage0 | Pump cooling | hub10 | Pump cooling Mode 1 | 43.5653 | 40007.4138 | 40007.4138 | 0.10483
Solution 4 | stage0 | Pump cooling | hub11 | Pump cooling Mode 1 | 266.7618 | 591625.2592 | 591625.2592 | 0.25317
Solution 4 | stage0 | Pump cooling | hub12 | Pump cooling Mode 1 | 4679.9342 | 9316324.8382 | 9316324.8382 | 0.22725
Solution 4 | stage0 | Pump cooling | hub13 | Pump cooling Mode 1 | 151.9881 | 69307.0831 | 69307.0831 | 0.052055
Solution 4 | stage0 | Pump cooling | hub14 | Pump cooling Mode 1 | 103.6616 | 51168.1813 | 51168.1813 | 0.056348
Solution 4 | stage0 | Pump cooling | hub2 | Pump cooling Mode 1 | 326.6423 | 228166.8433 | 228166.8433 | 0.07974
Solution 4 | stage0 | Pump cooling | hub3 | Pump cooling Mode 1 | 100.4378 | 131510.3058 | 131510.3058 | 0.14947
Solution 4 | stage0 | Pump cooling | hub4 | Pump cooling Mode 1 | 748.031 | 811707.9698 | 811707.9698 | 0.12387
Solution 4 | stage0 | Pump cooling | hub5 | Pump cooling Mode 1 | 380.9923 | 422265.8725 | 422265.8725 | 0.12652
Solution 4 | stage0 | Pump cooling | hub6 | Pump cooling Mode 1 | 127.8045 | 33799.1385 | 33799.1385 | 0.03019
Solution 4 | stage0 | Pump cooling | hub7 | Pump cooling Mode 1 | 264.3832 | 292396.6081 | 292396.6081 | 0.12625
Solution 4 | stage0 | Pump cooling | hub8 | Pump cooling Mode 1 | 267.1967 | 309788.5739 | 309788.5739 | 0.13235
Solution 4 | stage0 | Pump cooling | hub9 | Pump cooling Mode 1 | 1086.2268 | 1693852.2016 | 1693852.2016 | 0.17801
Solution 4 | stage0 | Pump DHW | hub1 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Pump DHW | hub10 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Pump DHW | hub11 | Pump DHW Mode 1 | 34.8297 | 157809.6407 | 157809.6407 | 0.51722
Solution 4 | stage0 | Pump DHW | hub12 | Pump DHW Mode 1 | 554.1475 | 3432869.3219 | 3432869.3219 | 0.70718
Solution 4 | stage0 | Pump DHW | hub13 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Pump DHW | hub14 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Pump DHW | hub2 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Pump DHW | hub3 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Pump DHW | hub4 | Pump DHW Mode 1 | 94.6748 | 355179.8886 | 355179.8886 | 0.42826
Solution 4 | stage0 | Pump DHW | hub5 | Pump DHW Mode 1 | 55.1879 | 207042.1928 | 207042.1928 | 0.42826
Solution 4 | stage0 | Pump DHW | hub6 | Pump DHW Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Pump DHW | hub7 | Pump DHW Mode 1 | 43.6957 | 163928.5463 | 163928.5463 | 0.42826
Solution 4 | stage0 | Pump DHW | hub8 | Pump DHW Mode 1 | 43.6957 | 163928.5463 | 163928.5463 | 0.42826
Solution 4 | stage0 | Pump DHW | hub9 | Pump DHW Mode 1 | 71.4402 | 268013.7936 | 268013.7936 | 0.42826
Solution 4 | stage0 | Pump SH | hub1 | Pump SH Mode 1 | 2304.5377 | 769002.1132 | 769002.1132 | 0.038093
Solution 4 | stage0 | Pump SH | hub10 | Pump SH Mode 1 | 135.9123 | 51886.8029 | 51886.8029 | 0.043581
Solution 4 | stage0 | Pump SH | hub11 | Pump SH Mode 1 | 218.5355 | 358030.5729 | 358030.5729 | 0.18702
Solution 4 | stage0 | Pump SH | hub12 | Pump SH Mode 1 | 2153.8699 | 7345736.8521 | 7345736.8521 | 0.38932
Solution 4 | stage0 | Pump SH | hub13 | Pump SH Mode 1 | 140.401 | 72255.5737 | 72255.5737 | 0.058749
Solution 4 | stage0 | Pump SH | hub14 | Pump SH Mode 1 | 142.1925 | 133678.2323 | 133678.2323 | 0.10732
Solution 4 | stage0 | Pump SH | hub2 | Pump SH Mode 1 | 279.8181 | 85065.6119 | 85065.6119 | 0.034704
Solution 4 | stage0 | Pump SH | hub3 | Pump SH Mode 1 | 58.7399 | 44423.8362 | 44423.8362 | 0.086333
Solution 4 | stage0 | Pump SH | hub4 | Pump SH Mode 1 | 273.5294 | 263452.5885 | 263452.5885 | 0.10995
Solution 4 | stage0 | Pump SH | hub5 | Pump SH Mode 1 | 136.167 | 116315.6148 | 116315.6148 | 0.097513
Solution 4 | stage0 | Pump SH | hub6 | Pump SH Mode 1 | 115.1239 | 65178.3221 | 65178.3221 | 0.06463
Solution 4 | stage0 | Pump SH | hub7 | Pump SH Mode 1 | 104.0534 | 100816.5425 | 100816.5425 | 0.1106
Solution 4 | stage0 | Pump SH | hub8 | Pump SH Mode 1 | 100.9653 | 97713.9952 | 97713.9952 | 0.11048
Solution 4 | stage0 | Pump SH | hub9 | Pump SH Mode 1 | 674.3585 | 577006.576 | 577006.576 | 0.097675
Solution 4 | stage0 | HEX SC ets | hub1 | HEX SC ets Mode 1 | 8.8973 | 768972.7946 | 768.9728 | 0.0098665
Solution 4 | stage0 | HEX SC ets | hub10 | HEX SC ets Mode 1 | 0.30656 | 83985.914 | 83.9859 | 0.031229
Solution 4 | stage0 | HEX SC ets | hub11 | HEX SC ets Mode 1 | 0.35302 | 519791.1934 | 519.7912 | 0.16809
Solution 4 | stage0 | HEX SC ets | hub12 | HEX SC ets Mode 1 | 9.3523 | 11327946.4268 | 11327.9464 | 0.13827
Solution 4 | stage0 | HEX SC ets | hub13 | HEX SC ets Mode 1 | 0.37588 | 116956.8928 | 116.9569 | 0.035509
Solution 4 | stage0 | HEX SC ets | hub14 | HEX SC ets Mode 1 | 0.4369 | 216237.9187 | 216.2379 | 0.056487
Solution 4 | stage0 | HEX SC ets | hub2 | HEX SC ets Mode 1 | 0.45201 | 137364.1103 | 137.3641 | 0.034692
Solution 4 | stage0 | HEX SC ets | hub3 | HEX SC ets Mode 1 | 0.10017 | 71803.7199 | 71.8037 | 0.081968
Solution 4 | stage0 | HEX SC ets | hub4 | HEX SC ets Mode 1 | 0.54157 | 635981.7679 | 635.9818 | 0.13395
Solution 4 | stage0 | HEX SC ets | hub5 | HEX SC ets Mode 1 | 0.51606 | 330000.9897 | 330.001 | 0.073006
Solution 4 | stage0 | HEX SC ets | hub6 | HEX SC ets Mode 1 | 0.18597 | 105395.3678 | 105.3954 | 0.064685
Solution 4 | stage0 | HEX SC ets | hub7 | HEX SC ets Mode 1 | 0.56142 | 276366.6527 | 276.3667 | 0.056237
Solution 4 | stage0 | HEX SC ets | hub8 | HEX SC ets Mode 1 | 0.59486 | 255042.6337 | 255.0426 | 0.048932
Solution 4 | stage0 | HEX SC ets | hub9 | HEX SC ets Mode 1 | 1.6167 | 989386.4026 | 989.3864 | 0.069848
Solution 4 | stage0 | ETS HP | hub1 | ETS HP Mode 1 | 2304.5377 | 147885.0218 | 769002.1132 | 0.038093
Solution 4 | stage0 | ETS HP | hub1 | ETS HP Mode 2 | 0.1 | 30.0764 | 150.3818 | 0.17167
Solution 4 | stage0 | ETS HP | hub1 | ETS HP Mode 3 | 2942.64 | 191359.8801 | 2870398.2014 | 0.11135
Solution 4 | stage0 | ETS HP | hub10 | ETS HP Mode 1 | 135.9123 | 9978.2313 | 51886.8029 | 0.043581
Solution 4 | stage0 | ETS HP | hub10 | ETS HP Mode 2 | 0.10506 | 29.5724 | 147.8622 | 0.16075
Solution 4 | stage0 | ETS HP | hub10 | ETS HP Mode 3 | 46.6128 | 2857.363 | 42860.4449 | 0.10497
Solution 4 | stage0 | ETS HP | hub11 | ETS HP Mode 1 | 218.5355 | 68852.0333 | 358030.5729 | 0.18702
Solution 4 | stage0 | ETS HP | hub11 | ETS HP Mode 2 | 132.8916 | 41600.1866 | 208000.9332 | 0.17867
Solution 4 | stage0 | ETS HP | hub11 | ETS HP Mode 3 | 237.2603 | 31252.9826 | 468794.7389 | 0.22556
Solution 4 | stage0 | ETS HP | hub12 | ETS HP Mode 1 | 2153.8699 | 1412641.7023 | 7345736.8521 | 0.38932
Solution 4 | stage0 | ETS HP | hub12 | ETS HP Mode 2 | 1989.4155 | 827360.7551 | 4136803.7753 | 0.23738
Solution 4 | stage0 | ETS HP | hub12 | ETS HP Mode 3 | 4243.7493 | 468937.1883 | 7034057.825 | 0.18921
Solution 4 | stage0 | ETS HP | hub13 | ETS HP Mode 1 | 140.401 | 13895.3026 | 72255.5737 | 0.058749
Solution 4 | stage0 | ETS HP | hub13 | ETS HP Mode 2 | 0.1 | 29.9774 | 149.8868 | 0.1711
Solution 4 | stage0 | ETS HP | hub13 | ETS HP Mode 3 | 162.7801 | 4952.5233 | 74287.8497 | 0.052097
Solution 4 | stage0 | ETS HP | hub14 | ETS HP Mode 1 | 142.1925 | 25707.3524 | 133678.2323 | 0.10732
Solution 4 | stage0 | ETS HP | hub14 | ETS HP Mode 2 | 0.1 | 29.4285 | 147.1425 | 0.16797
Solution 4 | stage0 | ETS HP | hub14 | ETS HP Mode 3 | 111.0017 | 3659.1411 | 54887.1163 | 0.056446
Solution 4 | stage0 | ETS HP | hub2 | ETS HP Mode 1 | 279.8181 | 16358.7715 | 85065.6119 | 0.034704
Solution 4 | stage0 | ETS HP | hub2 | ETS HP Mode 2 | 0.1 | 30.1478 | 150.7391 | 0.17208
Solution 4 | stage0 | ETS HP | hub2 | ETS HP Mode 3 | 349.9096 | 16289.401 | 244341.0156 | 0.079714
Solution 4 | stage0 | ETS HP | hub3 | ETS HP Mode 1 | 58.7399 | 8543.0454 | 44423.8362 | 0.086333
Solution 4 | stage0 | ETS HP | hub3 | ETS HP Mode 2 | 0.1 | 29.7385 | 148.6924 | 0.16974
Solution 4 | stage0 | ETS HP | hub3 | ETS HP Mode 3 | 107.5476 | 9388.7257 | 140830.8853 | 0.14948
Solution 4 | stage0 | ETS HP | hub4 | ETS HP Mode 1 | 273.5294 | 50663.9593 | 263452.5885 | 0.10995
Solution 4 | stage0 | ETS HP | hub4 | ETS HP Mode 2 | 239.3768 | 86257.7411 | 431288.7056 | 0.20568
Solution 4 | stage0 | ETS HP | hub4 | ETS HP Mode 3 | 647.5767 | 47009.7858 | 705146.787 | 0.1243
Solution 4 | stage0 | ETS HP | hub5 | ETS HP Mode 1 | 136.167 | 22368.3875 | 116315.6148 | 0.097513
Solution 4 | stage0 | ETS HP | hub5 | ETS HP Mode 2 | 139.5467 | 50171.9855 | 250859.9275 | 0.20521
Solution 4 | stage0 | ETS HP | hub5 | ETS HP Mode 3 | 318.4975 | 24485.9417 | 367289.1251 | 0.13164
Solution 4 | stage0 | ETS HP | hub6 | ETS HP Mode 1 | 115.1239 | 12534.2927 | 65178.3221 | 0.06463
Solution 4 | stage0 | ETS HP | hub6 | ETS HP Mode 2 | 0.1 | 28.8407 | 144.2034 | 0.16462
Solution 4 | stage0 | ETS HP | hub6 | ETS HP Mode 3 | 136.8691 | 2411.8765 | 36178.1475 | 0.030174
Solution 4 | stage0 | ETS HP | hub7 | ETS HP Mode 1 | 104.0534 | 19387.7966 | 100816.5425 | 0.1106
Solution 4 | stage0 | ETS HP | hub7 | ETS HP Mode 2 | 110.365 | 39695.0454 | 198475.2269 | 0.20529
Solution 4 | stage0 | ETS HP | hub7 | ETS HP Mode 3 | 212.3188 | 16433.2895 | 246499.3419 | 0.13253
Solution 4 | stage0 | ETS HP | hub8 | ETS HP Mode 1 | 100.9653 | 18791.1529 | 97713.9952 | 0.11048
Solution 4 | stage0 | ETS HP | hub8 | ETS HP Mode 2 | 110.365 | 39717.7271 | 198588.6356 | 0.20541
Solution 4 | stage0 | ETS HP | hub8 | ETS HP Mode 3 | 215.3332 | 17088.1334 | 256322.0006 | 0.13588
Solution 4 | stage0 | ETS HP | hub9 | ETS HP Mode 1 | 674.3585 | 110962.8031 | 577006.576 | 0.097675
Solution 4 | stage0 | ETS HP | hub9 | ETS HP Mode 2 | 180.5506 | 65944.4191 | 329722.0955 | 0.20847
Solution 4 | stage0 | ETS HP | hub9 | ETS HP Mode 3 | 1047.7462 | 108904.8838 | 1633573.2565 | 0.17798
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub1 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub1 | Gas Boiler (Linearized cost) Mode 2 | 2.2204e-13 | -2.2397e-11 | -2.0157e-11 | 0
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub10 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub10 | Gas Boiler (Linearized cost) Mode 2 | 3.4694e-15 | -1.7924e-12 | -1.6131e-12 | 0
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub11 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub11 | Gas Boiler (Linearized cost) Mode 2 | 2.7756e-14 | -1.3728e-11 | -1.2355e-11 | 0
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub12 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub12 | Gas Boiler (Linearized cost) Mode 2 | 4.4409e-13 | -2.8422e-10 | -2.558e-10 | 0
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub13 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub13 | Gas Boiler (Linearized cost) Mode 2 | 1.3878e-14 | -3.3274e-12 | -2.9947e-12 | 0
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub14 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub14 | Gas Boiler (Linearized cost) Mode 2 | 1.3878e-14 | -5.6267e-12 | -5.064e-12 | 0
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub2 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub2 | Gas Boiler (Linearized cost) Mode 2 | 5.5511e-14 | -3.0644e-12 | -2.7579e-12 | 0
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub3 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub3 | Gas Boiler (Linearized cost) Mode 2 | 6.9389e-15 | -2.5458e-12 | -2.2912e-12 | 0
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub4 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub4 | Gas Boiler (Linearized cost) Mode 2 | 2.7756e-14 | -9.8335e-12 | -8.8501e-12 | 0
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub5 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub5 | Gas Boiler (Linearized cost) Mode 2 | 1.3878e-14 | -4.7082e-12 | -4.2374e-12 | 0
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub6 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub6 | Gas Boiler (Linearized cost) Mode 2 | 6.9389e-15 | -1.9788e-12 | -1.7809e-12 | 0
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub7 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub7 | Gas Boiler (Linearized cost) Mode 2 | 1.3878e-14 | -3.6853e-12 | -3.3167e-12 | 0
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub8 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub8 | Gas Boiler (Linearized cost) Mode 2 | 1.3878e-14 | -3.4722e-12 | -3.125e-12 | 0
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub9 | Gas Boiler (Linearized cost) Mode 1 | 0 | 0 | 0 | 0
Solution 4 | stage0 | Gas Boiler (Linearized cost) | hub9 | Gas Boiler (Linearized cost) Mode 2 | 5.5511e-14 | -2.3529e-11 | -2.1176e-11 | 0
Solution 4 | stage0 | rooftop to pv | plant | rooftop to pv Mode 1 | 6584.7276 | 8694079.8505 | 8694079.8505 | 0.15072

## Storages
Solution | Stage | Name | Hub | Capacity (kWh) | Charging (kWh/year) | Discharging (kWh/year) | Cycles
Solution 1 | stage0 | battery | plant | 0 | 0 | 0 | 0
Solution 1 | stage0 | Generic Hot Water Storage hub1 | hub1 | 0.279 | 23.3449 | 0 | 0
Solution 1 | stage0 | Generic Hot Water Storage hub2 | hub2 | 0.198 | 16.4957 | 0 | 0
Solution 1 | stage0 | Generic Hot Water Storage hub3 | hub3 | 0.667 | 58.8476 | 0 | 0
Solution 1 | stage0 | Generic Hot Water Storage hub4 | hub4 | 494.42 | 174392.7481 | 130399.7664 | 263.7429
Solution 1 | stage0 | Generic Hot Water Storage hub5 | hub5 | 270.184 | 96914.9072 | 73008.4277 | 270.2174
Solution 1 | stage0 | Generic Hot Water Storage hub6 | hub6 | 0.274 | 18.1295 | 8.8339e-10 | 3.3086e-09
Solution 1 | stage0 | Generic Hot Water Storage hub7 | hub7 | 245.254 | 80753.9614 | 60261.2024 | 245.7094
Solution 1 | stage0 | Generic Hot Water Storage hub8 | hub8 | 250.112 | 83156.9817 | 61720.4007 | 246.771
Solution 1 | stage0 | Generic Hot Water Storage hub9 | hub9 | 640.851 | 170847.2933 | 112292.9706 | 175.2248
Solution 1 | stage0 | Generic Hot Water Storage hub10 | hub10 | 0.305 | 18.9083 | 0 | 0
Solution 1 | stage0 | Generic Hot Water Storage hub11 | hub11 | 180.852 | 62152.2713 | 47718.5448 | 263.8541
Solution 1 | stage0 | Generic Hot Water Storage hub12 | hub12 | 3112.219 | 1149918.7859 | 918142.2649 | 295.0121
Solution 1 | stage0 | Generic Hot Water Storage hub13 | hub13 | 0.278 | 21.7523 | 0 | 0
Solution 1 | stage0 | Generic Hot Water Storage hub14 | hub14 | 0.167 | 10.102 | 5.5618e-10 | 3.4761e-09
Solution 1 | stage0 | Generic Borehole | plant | 9500000 | 11178645.5383 | 9715914.2315 | 1.0227
Solution 2 | stage0 | battery | plant | 0.1 | 73.6681 | 73.6681 | 736.6814
Solution 2 | stage0 | Generic Hot Water Storage hub1 | hub1 | 0.277 | 26.6951 | 0 | 0
Solution 2 | stage0 | Generic Hot Water Storage hub2 | hub2 | 0.191 | 17.758 | 0 | 0
Solution 2 | stage0 | Generic Hot Water Storage hub3 | hub3 | 0.664 | 61.5175 | 0 | 0
Solution 2 | stage0 | Generic Hot Water Storage hub4 | hub4 | 524.908 | 180843.4822 | 134612.2022 | 256.4491
Solution 2 | stage0 | Generic Hot Water Storage hub5 | hub5 | 285.427 | 100472.7484 | 75269.3366 | 263.7078
Solution 2 | stage0 | Generic Hot Water Storage hub6 | hub6 | 0.272 | 21.7292 | 0 | 0
Solution 2 | stage0 | Generic Hot Water Storage hub7 | hub7 | 234.286 | 80205.7916 | 60064.445 | 256.3723
Solution 2 | stage0 | Generic Hot Water Storage hub8 | hub8 | 249.089 | 84032.5762 | 62362.1172 | 250.3608
Solution 2 | stage0 | Generic Hot Water Storage hub9 | hub9 | 566.07 | 164066.0938 | 114305.1381 | 201.9276
Solution 2 | stage0 | Generic Hot Water Storage hub10 | hub10 | 0.303 | 23.8608 | 0 | 0
Solution 2 | stage0 | Generic Hot Water Storage hub11 | hub11 | 180.852 | 62713.7612 | 48196.0222 | 266.4943
Solution 2 | stage0 | Generic Hot Water Storage hub12 | hub12 | 3173.361 | 1167531.1498 | 927664.2409 | 292.3286
Solution 2 | stage0 | Generic Hot Water Storage hub13 | hub13 | 0.274 | 24.7809 | 0 | 0
Solution 2 | stage0 | Generic Hot Water Storage hub14 | hub14 | 0.166 | 12.5947 | 0 | 0
Solution 2 | stage0 | Generic Borehole | plant | 9500000 | 11166223.9238 | 9703240.4079 | 1.0214
Solution 3 | stage0 | battery | plant | 4551.149 | 1688829.0412 | 1688829.0412 | 371.0775
Solution 3 | stage0 | Generic Hot Water Storage hub1 | hub1 | 0.271 | 25.651 | 0 | 0
Solution 3 | stage0 | Generic Hot Water Storage hub2 | hub2 | 0.744 | 70.3174 | 0 | 0
Solution 3 | stage0 | Generic Hot Water Storage hub3 | hub3 | 0.687 | 65.3325 | 0 | 0
Solution 3 | stage0 | Generic Hot Water Storage hub4 | hub4 | 467.977 | 175382.6556 | 139063.7318 | 297.1593
Solution 3 | stage0 | Generic Hot Water Storage hub5 | hub5 | 247.856 | 95834.4436 | 76712.7658 | 309.5054
Solution 3 | stage0 | Generic Hot Water Storage hub6 | hub6 | 0.267 | 23.2499 | 0 | 0
Solution 3 | stage0 | Generic Hot Water Storage hub7 | hub7 | 203.082 | 78698.5602 | 63215.2757 | 311.2796
Solution 3 | stage0 | Generic Hot Water Storage hub8 | hub8 | 213.646 | 81227.2773 | 64800.9842 | 303.3101
Solution 3 | stage0 | Generic Hot Water Storage hub9 | hub9 | 501.866 | 159206.6523 | 118266.3552 | 235.6533
Solution 3 | stage0 | Generic Hot Water Storage hub10 | hub10 | 0.427 | 38.0022 | 0 | 0
Solution 3 | stage0 | Generic Hot Water Storage hub11 | hub11 | 203.081 | 62216.3375 | 46756.7371 | 230.2369
Solution 3 | stage0 | Generic Hot Water Storage hub12 | hub12 | 4289.786 | 1456935.6908 | 1128794.4283 | 263.1354
Solution 3 | stage0 | Generic Hot Water Storage hub13 | hub13 | 0.266 | 24.4247 | 0 | 0
Solution 3 | stage0 | Generic Hot Water Storage hub14 | hub14 | 0.27 | 23.6191 | 0 | 0
Solution 3 | stage0 | Generic Borehole | plant | 9500000 | 11203658.9173 | 9741435.4834 | 1.0254
Solution 4 | stage0 | battery | plant | 8607 | 3167703.0917 | 3167703.0917 | 368.038
Solution 4 | stage0 | Generic Hot Water Storage hub1 | hub1 | 1.566 | 150.3818 | 0 | 0
Solution 4 | stage0 | Generic Hot Water Storage hub2 | hub2 | 1.566 | 150.7391 | 0 | 0
Solution 4 | stage0 | Generic Hot Water Storage hub3 | hub3 | 1.547 | 148.6924 | 0 | 0
Solution 4 | stage0 | Generic Hot Water Storage hub4 | hub4 | 1139 | 259102.8887 | 182994.0716 | 160.662
Solution 4 | stage0 | Generic Hot Water Storage hub5 | hub5 | 664 | 150425.9243 | 106608.1897 | 160.5545
Solution 4 | stage0 | Generic Hot Water Storage hub6 | hub6 | 1.489 | 144.2034 | 0 | 0
Solution 4 | stage0 | Generic Hot Water Storage hub7 | hub7 | 525 | 117994.0174 | 83447.3368 | 158.9473
Solution 4 | stage0 | Generic Hot Water Storage hub8 | hub8 | 525 | 119194.7831 | 84534.6939 | 161.0185
Solution 4 | stage0 | Generic Hot Water Storage hub9 | hub9 | 859 | 203923.0075 | 142214.7056 | 165.5584
Solution 4 | stage0 | Generic Hot Water Storage hub10 | hub10 | 1.538 | 147.8622 | 0 | 0
Solution 4 | stage0 | Generic Hot Water Storage hub11 | hub11 | 633 | 126352.0358 | 76160.7433 | 120.3171
Solution 4 | stage0 | Generic Hot Water Storage hub12 | hub12 | 11220 | 2356452.4585 | 1652518.0051 | 147.2832
Solution 4 | stage0 | Generic Hot Water Storage hub13 | hub13 | 1.558 | 149.8868 | 0 | 0
Solution 4 | stage0 | Generic Hot Water Storage hub14 | hub14 | 1.53 | 147.1425 | 0 | 0
Solution 4 | stage0 | Generic Borehole | plant | 9113535.494 | 11468186.1182 | 10011333.658 | 1.0538

## Networks
Solution | Stage | Name | Link | Source hub | Sink hub | Capacity (kW) | Energy from-to (kWh/year) | Energy to-from (kWh/year)
Solution 1 | stage0 | Anergy | hub1_to_hub2_Anergy | hub1 | hub2 | 7735.822 | 6923056.3351 | 11522845.3534
Solution 1 | stage0 | Anergy | hub3_to_hub4_Anergy | hub3 | hub4 | 7405.688 | 6831310.9327 | 11137525.2353
Solution 1 | stage0 | Anergy | hub5_to_hub6_Anergy | hub5 | hub6 | 6515.179 | 6434302.9158 | 10083184.2495
Solution 1 | stage0 | Anergy | hub7_to_hub8_Anergy | hub7 | hub8 | 6244.39 | 6273331.3755 | 9811317.3318
Solution 1 | stage0 | Anergy | hub9_to_hub10_Anergy | hub9 | hub10 | 5034.41 | 5741383.1737 | 7940795.0693
Solution 1 | stage0 | Anergy | hub11_to_hub12_Anergy | hub11 | hub12 | 4749.837 | 5469957.8938 | 7416542.0275
Solution 1 | stage0 | Anergy | hub13_to_hub14_Anergy | hub13 | hub14 | 113.848 | 105264.5345 | 56222.2696
Solution 1 | stage0 | pv_loop | hub1_to_hub2_pv_loop | hub1 | hub2 | 39.038 | 50810.9322 | 0
Solution 1 | stage0 | pv_loop | hub3_to_hub4_pv_loop | hub3 | hub4 | 18.755 | 31829.516 | 0
Solution 1 | stage0 | pv_loop | hub5_to_hub6_pv_loop | hub5 | hub6 | 18.755 | 28444.7214 | 0
Solution 1 | stage0 | pv_loop | hub7_to_hub8_pv_loop | hub7 | hub8 | 5.003 | 2574.1332 | 0
Solution 1 | stage0 | pv_loop | hub9_to_hub10_pv_loop | hub9 | hub10 | 5.003 | 1871.6137 | 0
Solution 1 | stage0 | pv_loop | hub11_to_hub12_pv_loop | hub11 | hub12 | 5.003 | 1066.4892 | 0
Solution 1 | stage0 | pv_loop | hub13_to_hub14_pv_loop | hub13 | hub14 | 3.354 | 97.6379 | 0
Solution 1 | stage0 | Anergy | plant_to_hub1_Anergy | plant | hub1 | 10491.356 | 7094385.9612 | 14263229.8192
Solution 1 | stage0 | Anergy | hub2_to_hub3_Anergy | hub2 | hub3 | 7515.273 | 6865636.2965 | 11281600.8705
Solution 1 | stage0 | Anergy | hub4_to_hub5_Anergy | hub4 | hub5 | 6773.377 | 6563499.9909 | 10438475.2594
Solution 1 | stage0 | Anergy | hub6_to_hub7_Anergy | hub6 | hub7 | 6440.274 | 6383351.9706 | 10046395.5258
Solution 1 | stage0 | Anergy | hub8_to_hub9_Anergy | hub8 | hub9 | 6102.402 | 6174251.3897 | 9567174.1989
Solution 1 | stage0 | Anergy | hub10_to_hub11_Anergy | hub10 | hub11 | 4987.749 | 5700569.7224 | 7896887.7046
Solution 1 | stage0 | Anergy | hub12_to_hub13_Anergy | hub12 | hub13 | 228.685 | 161957.8688 | 132369.271
Solution 1 | stage0 | pv_loop | plant_to_hub1_pv_loop | plant | hub1 | 76.734 | 101314.9104 | 0
Solution 1 | stage0 | pv_loop | hub2_to_hub3_pv_loop | hub2 | hub3 | 20.959 | 36307.0377 | 0
Solution 1 | stage0 | pv_loop | hub4_to_hub5_pv_loop | hub4 | hub5 | 18.755 | 29376.9143 | 0
Solution 1 | stage0 | pv_loop | hub6_to_hub7_pv_loop | hub6 | hub7 | 5.003 | 2590.5332 | 0
Solution 1 | stage0 | pv_loop | hub8_to_hub9_pv_loop | hub8 | hub9 | 5.003 | 2515.4255 | 0
Solution 1 | stage0 | pv_loop | hub10_to_hub11_pv_loop | hub10 | hub11 | 5.003 | 1621.165 | 0
Solution 1 | stage0 | pv_loop | hub12_to_hub13_pv_loop | hub12 | hub13 | 3.354 | 103.4379 | 0
Solution 2 | stage0 | Anergy | hub1_to_hub2_Anergy | hub1 | hub2 | 7736.554 | 6936029.5493 | 11536262.7835
Solution 2 | stage0 | Anergy | hub3_to_hub4_Anergy | hub3 | hub4 | 7406.42 | 6845394.0936 | 11152054.6863
Solution 2 | stage0 | Anergy | hub5_to_hub6_Anergy | hub5 | hub6 | 6508.472 | 6446388.8266 | 10097374.9486
Solution 2 | stage0 | Anergy | hub7_to_hub8_Anergy | hub7 | hub8 | 6240.837 | 6284048.4551 | 9823789.04
Solution 2 | stage0 | Anergy | hub9_to_hub10_Anergy | hub9 | hub10 | 5029.646 | 5750503.5518 | 7945631.8367
Solution 2 | stage0 | Anergy | hub11_to_hub12_Anergy | hub11 | hub12 | 4745.175 | 5479254.6582 | 7421593.0692
Solution 2 | stage0 | Anergy | hub13_to_hub14_Anergy | hub13 | hub14 | 113.848 | 105266.4012 | 56222.73
Solution 2 | stage0 | pv_loop | hub1_to_hub2_pv_loop | hub1 | hub2 | 2262.841 | 3518601.2825 | 0
Solution 2 | stage0 | pv_loop | hub3_to_hub4_pv_loop | hub3 | hub4 | 2203.512 | 3306774.0646 | 0
Solution 2 | stage0 | pv_loop | hub5_to_hub6_pv_loop | hub5 | hub6 | 1985.018 | 3259493.6153 | 0
Solution 2 | stage0 | pv_loop | hub7_to_hub8_pv_loop | hub7 | hub8 | 1927.137 | 3118408.1094 | 0
Solution 2 | stage0 | pv_loop | hub9_to_hub10_pv_loop | hub9 | hub10 | 1622.645 | 2857445.3349 | 0
Solution 2 | stage0 | pv_loop | hub11_to_hub12_pv_loop | hub11 | hub12 | 1540.416 | 2556597.2275 | 0
Solution 2 | stage0 | pv_loop | hub13_to_hub14_pv_loop | hub13 | hub14 | 12.192 | 24839.5804 | 0
Solution 2 | stage0 | Anergy | plant_to_hub1_Anergy | plant | hub1 | 10492.088 | 7103874.0756 | 14273160.2787
Solution 2 | stage0 | Anergy | hub2_to_hub3_Anergy | hub2 | hub3 | 7516.005 | 6879532.3908 | 11295941.7924
Solution 2 | stage0 | Anergy | hub4_to_hub5_Anergy | hub4 | hub5 | 6748.552 | 6576751.402 | 10453201.0556
Solution 2 | stage0 | Anergy | hub6_to_hub7_Anergy | hub6 | hub7 | 6415.72 | 6395726.0086 | 10060876.3815
Solution 2 | stage0 | Anergy | hub8_to_hub9_Anergy | hub8 | hub9 | 6098.623 | 6183346.1292 | 9578010.1339
Solution 2 | stage0 | Anergy | hub10_to_hub11_Anergy | hub10 | hub11 | 4983.087 | 5709671.9314 | 7901709.1489
Solution 2 | stage0 | Anergy | hub12_to_hub13_Anergy | hub12 | hub13 | 228.687 | 162046.1162 | 132371.5577
Solution 2 | stage0 | pv_loop | plant_to_hub1_pv_loop | plant | hub1 | 3071.708 | 4149820.6557 | 0
Solution 2 | stage0 | pv_loop | hub2_to_hub3_pv_loop | hub2 | hub3 | 2239.642 | 3446305.3385 | 0
Solution 2 | stage0 | pv_loop | hub4_to_hub5_pv_loop | hub4 | hub5 | 2061.665 | 3270395.281 | 0
Solution 2 | stage0 | pv_loop | hub6_to_hub7_pv_loop | hub6 | hub7 | 1982.952 | 3211529.5235 | 0
Solution 2 | stage0 | pv_loop | hub8_to_hub9_pv_loop | hub8 | hub9 | 1867.648 | 2996135.5309 | 0
Solution 2 | stage0 | pv_loop | hub10_to_hub11_pv_loop | hub10 | hub11 | 1621.79 | 2822315.4519 | 0
Solution 2 | stage0 | pv_loop | hub12_to_hub13_pv_loop | hub12 | hub13 | 24.562 | 44173.5431 | 0
Solution 3 | stage0 | Anergy | hub1_to_hub2_Anergy | hub1 | hub2 | 7902.482 | 6934219.2999 | 11497559.8394
Solution 3 | stage0 | Anergy | hub3_to_hub4_Anergy | hub3 | hub4 | 7557.576 | 6844741.8836 | 11114545.7759
Solution 3 | stage0 | Anergy | hub5_to_hub6_Anergy | hub5 | hub6 | 6447.102 | 6441990.6817 | 10045812.103
Solution 3 | stage0 | Anergy | hub7_to_hub8_Anergy | hub7 | hub8 | 6228.776 | 6278994.1798 | 9768484.8098
Solution 3 | stage0 | Anergy | hub9_to_hub10_Anergy | hub9 | hub10 | 4945.941 | 5744773.4361 | 7880271.2982
Solution 3 | stage0 | Anergy | hub11_to_hub12_Anergy | hub11 | hub12 | 4654.539 | 5471870.5565 | 7355049.8913
Solution 3 | stage0 | Anergy | hub13_to_hub14_Anergy | hub13 | hub14 | 113.848 | 105269.4559 | 56218.904
Solution 3 | stage0 | pv_loop | hub1_to_hub2_pv_loop | hub1 | hub2 | 3157.015 | 6841308.8479 | 0
Solution 3 | stage0 | pv_loop | hub3_to_hub4_pv_loop | hub3 | hub4 | 2995.695 | 6479556.5127 | 0
Solution 3 | stage0 | pv_loop | hub5_to_hub6_pv_loop | hub5 | hub6 | 2644.727 | 6177432.7892 | 0
Solution 3 | stage0 | pv_loop | hub7_to_hub8_pv_loop | hub7 | hub8 | 2557.567 | 5965935.1857 | 0
Solution 3 | stage0 | pv_loop | hub9_to_hub10_pv_loop | hub9 | hub10 | 2013.806 | 5219357.8132 | 0
Solution 3 | stage0 | pv_loop | hub11_to_hub12_pv_loop | hub11 | hub12 | 1887.682 | 4863645.3052 | 0
Solution 3 | stage0 | pv_loop | hub13_to_hub14_pv_loop | hub13 | hub14 | 58.168 | 78165.1388 | 0
Solution 3 | stage0 | Anergy | plant_to_hub1_Anergy | plant | hub1 | 10658.016 | 7085296.787 | 14217691.3673
Solution 3 | stage0 | Anergy | hub2_to_hub3_Anergy | hub2 | hub3 | 7667.16 | 6878483.098 | 11258033.6536
Solution 3 | stage0 | Anergy | hub4_to_hub5_Anergy | hub4 | hub5 | 6813.074 | 6573409.2081 | 10406575.734
Solution 3 | stage0 | Anergy | hub6_to_hub7_Anergy | hub6 | hub7 | 6436.577 | 6391039.4788 | 10009025.7524
Solution 3 | stage0 | Anergy | hub8_to_hub9_Anergy | hub8 | hub9 | 6063.171 | 6178067.5852 | 9519102.4022
Solution 3 | stage0 | Anergy | hub10_to_hub11_Anergy | hub10 | hub11 | 4899.449 | 5703979.1847 | 7836394.7887
Solution 3 | stage0 | Anergy | hub12_to_hub13_Anergy | hub12 | hub13 | 228.626 | 162072.071 | 132366.5097
Solution 3 | stage0 | pv_loop | plant_to_hub1_pv_loop | plant | hub1 | 4162.183 | 8160581.2497 | 0
Solution 3 | stage0 | pv_loop | hub2_to_hub3_pv_loop | hub2 | hub3 | 3083.452 | 6676634.3585 | 0
Solution 3 | stage0 | pv_loop | hub4_to_hub5_pv_loop | hub4 | hub5 | 2759.51 | 6285374.3188 | 0
Solution 3 | stage0 | pv_loop | hub6_to_hub7_pv_loop | hub6 | hub7 | 2642.683 | 6121914.4989 | 0
Solution 3 | stage0 | pv_loop | hub8_to_hub9_pv_loop | hub8 | hub9 | 2478.145 | 5792419.5796 | 0
Solution 3 | stage0 | pv_loop | hub10_to_hub11_pv_loop | hub10 | hub11 | 1998.728 | 5166084.5832 | 0
Solution 3 | stage0 | pv_loop | hub12_to_hub13_pv_loop | hub12 | hub13 | 62.151 | 138069.0707 | 0
Solution 4 | stage0 | Anergy | hub1_to_hub2_Anergy | hub1 | hub2 | 7439.128 | 7133144.4518 | 11379257.84
Solution 4 | stage0 | Anergy | hub3_to_hub4_Anergy | hub3 | hub4 | 7235.002 | 7050429.212 | 11003463.9572
Solution 4 | stage0 | Anergy | hub5_to_hub6_Anergy | hub5 | hub6 | 6244.156 | 6614187.5836 | 9938444.8744
Solution 4 | stage0 | Anergy | hub7_to_hub8_Anergy | hub7 | hub8 | 6026.393 | 6442602.0641 | 9663326.9026
Solution 4 | stage0 | Anergy | hub9_to_hub10_Anergy | hub9 | hub10 | 4827.647 | 5902989.4574 | 7792347.0927
Solution 4 | stage0 | Anergy | hub11_to_hub12_Anergy | hub11 | hub12 | 4542.669 | 5622419.1938 | 7281345.982
Solution 4 | stage0 | Anergy | hub13_to_hub14_Anergy | hub13 | hub14 | 113.848 | 105307.7587 | 56180.6304
Solution 4 | stage0 | pv_loop | hub1_to_hub2_pv_loop | hub1 | hub2 | 4372.873 | 9618043.7727 | 0
Solution 4 | stage0 | pv_loop | hub3_to_hub4_pv_loop | hub3 | hub4 | 4138.696 | 9130723.3543 | 0
Solution 4 | stage0 | pv_loop | hub5_to_hub6_pv_loop | hub5 | hub6 | 3674.015 | 8253402.3208 | 0
Solution 4 | stage0 | pv_loop | hub7_to_hub8_pv_loop | hub7 | hub8 | 3485.194 | 7995790.6951 | 0
Solution 4 | stage0 | pv_loop | hub9_to_hub10_pv_loop | hub9 | hub10 | 2612.48 | 6395201.0915 | 0
Solution 4 | stage0 | pv_loop | hub11_to_hub12_pv_loop | hub11 | hub12 | 2388.235 | 5984370.4187 | 0
Solution 4 | stage0 | pv_loop | hub13_to_hub14_pv_loop | hub13 | hub14 | 60.491 | 71551.0898 | 0
Solution 4 | stage0 | Anergy | plant_to_hub1_Anergy | plant | hub1 | 9948.757 | 7257260.8436 | 14072349.1314
Solution 4 | stage0 | Anergy | hub2_to_hub3_Anergy | hub2 | hub3 | 7344.586 | 7081915.2013 | 11144387.4233
Solution 4 | stage0 | Anergy | hub4_to_hub5_Anergy | hub4 | hub5 | 6570.82 | 6757658.0041 | 10297532.297
Solution 4 | stage0 | Anergy | hub6_to_hub7_Anergy | hub6 | hub7 | 6244.156 | 6563426.5063 | 9901958.2467
Solution 4 | stage0 | Anergy | hub8_to_hub9_Anergy | hub8 | hub9 | 5805.539 | 6333653.5981 | 9416130.1878
Solution 4 | stage0 | Anergy | hub10_to_hub11_Anergy | hub10 | hub11 | 4786.013 | 5862302.7203 | 7748646.4185
Solution 4 | stage0 | Anergy | hub12_to_hub13_Anergy | hub12 | hub13 | 228.561 | 162219.0072 | 132264.0155
Solution 4 | stage0 | pv_loop | plant_to_hub1_pv_loop | plant | hub1 | 5957.135 | 11811668.1236 | 0
Solution 4 | stage0 | pv_loop | hub2_to_hub3_pv_loop | hub2 | hub3 | 4229.076 | 9393080.2046 | 0
Solution 4 | stage0 | pv_loop | hub4_to_hub5_pv_loop | hub4 | hub5 | 3829.827 | 8557004.373 | 0
Solution 4 | stage0 | pv_loop | hub6_to_hub7_pv_loop | hub6 | hub7 | 3600.751 | 8198599.9324 | 0
Solution 4 | stage0 | pv_loop | hub8_to_hub9_pv_loop | hub8 | hub9 | 3381.109 | 7794685.3216 | 0
Solution 4 | stage0 | pv_loop | hub10_to_hub11_pv_loop | hub10 | hub11 | 2579.626 | 6348212.9267 | 0
Solution 4 | stage0 | pv_loop | hub12_to_hub13_pv_loop | hub12 | hub13 | 124.501 | 128841.7615 | 0

## Intrahubs
Solution | Stage | Name | Hub | Capacity (kW) | Energy in (kWh/year) | Energy out (kWh/year)