## Whole year
From | To | kWh
PV and bettery | Electricity | 10612736.799
Electricity | Buildings fans + non HVAC | 9361383.7879
Electricity | Pump coo | 427071.271
Electricity | Pump hea | 168391.0279
Electricity | Pump DHW | 1125.222
Electricity | ETS | 4762481.5164
Electricity | Central plant chiller | 3134861.9417
Electricity | Dry cooler | 37363.773
Electricity | Pump district | 1707840.6152
Heat ambient | Dry cooler | 2916925.8327
TEN | Central plant chiller | 9632461.8009
Dry cooler | Heat ambient | 12171623.1653
Central plant chiller | TEN | 3576208.4405
Economiser | TEN | 48166.7219
Borefield | TEN | 8191767.8661
Ground | TEN | 390241.5578
ETS | Pump district | 15918445.086
TEN | Economiser | 25570.906
TEN | Borefield | 8063011.6713
TEN | Ground | 1076708.4867
Pump district | ETS | 9222530.2383
Pump coo | ETS | 16911643.5346
ETS | Pump hea | 10056633.8056
ETS | DHW | 4864814.4907

## Winter
From | To | kWh
PV and bettery | Electricity | 2632858.689
Electricity | Buildings fans + non HVAC | 3503815.7933
Electricity | Pump coo | 84927.5361
Electricity | Pump hea | 90142.4005
Electricity | Pump DHW | 430.735
Electricity | ETS | 2267835.7276
Electricity | Central plant chiller | 422996.1914
Electricity | Dry cooler | 4906.5506
Electricity | Pump district | 1202965.6176
Heat ambient | Dry cooler | 1633985.8518
TEN | Central plant chiller | 70729.949
Dry cooler | Heat ambient | 83529.9454
Central plant chiller | TEN | 1993490.3709
Economiser | TEN | 134.0736
Borefield | TEN | 4574555.5783
Ground | TEN | 47037.3741
ETS | Pump district | 861371.2632
TEN | Economiser | 25570.6815
TEN | Borefield | 84848.6256
TEN | Ground | 470922.3243
Pump district | ETS | 6832519.1503
Pump coo | ETS | 846992.9392
ETS | Pump hea | 7167326.0405
ETS | DHW | 2030911.169

## Spring
From | To | kWh
PV and bettery | Electricity | 3611313.025
Electricity | Buildings fans + non HVAC | 2503991.5601
Electricity | Pump coo | 137509.8245
Electricity | Pump hea | 36926.526
Electricity | Pump DHW | 303.7397
Electricity | ETS | 1013057.4106
Electricity | Central plant chiller | 895009.861
Electricity | Dry cooler | 17362.58
Electricity | Pump district | 300190.6255
Heat ambient | Dry cooler | 555922.9406
TEN | Central plant chiller | 3427843.3264
Dry cooler | Heat ambient | 4276221.6348
Central plant chiller | TEN | 657593.8076
Economiser | TEN | 0
Borefield | TEN | 3007150.0161
Ground | TEN | 120028.7508
ETS | Pump district | 5095320.8702
TEN | Economiser | 0
TEN | Borefield | 3614326.9611
TEN | Ground | 392742.8991
Pump district | ETS | 1350821.2219
Pump coo | ETS | 5554481.3323
ETS | Pump hea | 1447241.6907
ETS | DHW | 1383142.844

## Summer
From | To | kWh
PV and bettery | Electricity | 2985749.657
Electricity | Buildings fans + non HVAC | 1936567.558
Electricity | Pump coo | 132145.0986
Electricity | Pump hea | 18710.8065
Electricity | Pump DHW | 217.855
Electricity | ETS | 946717.9215
Electricity | Central plant chiller | 1431970.4645
Electricity | Dry cooler | 9574.8454
Electricity | Pump district | 68165.6779
Heat ambient | Dry cooler | 0
TEN | Central plant chiller | 4876128.9291
Dry cooler | Heat ambient | 6374173.2454
Central plant chiller | TEN | 0
Economiser | TEN | 48032.6482
Borefield | TEN | 177464.7297
Ground | TEN | 102803.3748
ETS | Pump district | 7576664.2796
TEN | Economiser | 0.22449
TEN | Borefield | 2839789.7644
TEN | Ground | 89883.385
Pump district | ETS | 113923.2334
Pump coo | ETS | 7982391.8658
ETS | Pump hea | 461273.8499
ETS | DHW | 803194.6726

## Fall
From | To | kWh
PV and bettery | Electricity | 1382815.428
Electricity | Buildings fans + non HVAC | 1417008.8765
Electricity | Pump coo | 72488.8118
Electricity | Pump hea | 22611.2949
Electricity | Pump DHW | 172.8924
Electricity | ETS | 534870.4566
Electricity | Central plant chiller | 384885.4248
Electricity | Dry cooler | 5519.797
Electricity | Pump district | 136518.6942
Heat ambient | Dry cooler | 726971.4754
TEN | Central plant chiller | 1257730.3139
Dry cooler | Heat ambient | 1437667.0173
Central plant chiller | TEN | 925067.9556
Economiser | TEN | 0
Borefield | TEN | 432531.2941
Ground | TEN | 120359.234
ETS | Pump district | 2385057.5607
TEN | Economiser | 0
TEN | Borefield | 1524032.1029
TEN | Ground | 123150.8584
Pump district | ETS | 925174.3814
Pump coo | ETS | 2527777.3973
ETS | Pump hea | 980792.2244
ETS | DHW | 647565.8051