## Whole year
From | To | Energy carrier | kWh
Electricity import | ETS chiller | electricity | 5087859.6621
Electricity import | Central chiller | electricity | 3121593.7047
Dry cooler | Central chiller | plant heat rejection | 11980457.505
Dry cooler | Central chiller | plant cooling rejection | 2605140.0624
Dry cooler | Economizer | plant heat rejection | 41486.4482
Dry cooler | Economizer | plant cooling rejection | 85562.6302
Central chiller | Reservoir loop | plant cooling | 9544038.1816
Central chiller | Reservoir loop | plant heating | 3290298.5346
Reservoir loop | ETS chiller | ETS heat rejection | 15683554.4759
Reservoir loop | ETS chiller | ETS cooling rejection | 8444299.5372
ETS chiller | Cooling load | cooling load | 16124971.5251
ETS chiller | Heating load | space heating load | 10053002.1421
ETS chiller | DHW load | domestic hot water | 4037508.9384
Reservoir loop | Ground | ground anergy | 1099048.3999
Ground | Reservoir loop | ground anergy | 341111.8187
Economizer | Reservoir loop | plant heating | 85562.6302
Economizer | Reservoir loop | plant cooling | 41486.4482
Borefield center | Reservoir loop | borefield center anergy | 6435065.0302
Reservoir loop | Borefield center | borefield center anergy | 6543748.1485
Borefield perimeter | Reservoir loop | borefield perimeter anergy | 1350925.2142
Reservoir loop | Borefield perimeter | borefield perimeter anergy | 1288548.3081

## Winter
From | To | Energy carrier | kWh
Electricity import | ETS chiller | electricity | 2056562.5504
Electricity import | Central chiller | electricity | 426859.8937
Dry cooler | Central chiller | plant heat rejection | 79718.9384
Dry cooler | Central chiller | plant cooling rejection | 1513445.0404
Dry cooler | Economizer | plant heat rejection | 40452.986
Dry cooler | Economizer | plant cooling rejection | 1665.6323
Central chiller | Reservoir loop | plant cooling | 71336.8277
Central chiller | Reservoir loop | plant heating | 1931915.3071
Reservoir loop | ETS chiller | ETS heat rejection | 731261.6237
Reservoir loop | ETS chiller | ETS cooling rejection | 6618853.9626
ETS chiller | Cooling load | cooling load | 842596.3235
ETS chiller | Heating load | space heating load | 7162602.1878
ETS chiller | DHW load | domestic hot water | 1688821.7011
Reservoir loop | Ground | ground anergy | 481070.5272
Ground | Reservoir loop | ground anergy | 46385.6454
Economizer | Reservoir loop | plant heating | 1665.6323
Economizer | Reservoir loop | plant cooling | 40452.986
Borefield center | Reservoir loop | borefield center anergy | 3521936.187
Reservoir loop | Borefield center | borefield center anergy | 38043.0885
Borefield perimeter | Reservoir loop | borefield perimeter anergy | 999639.5931
Reservoir loop | Borefield perimeter | borefield perimeter anergy | 50035.3573

## Spring
From | To | Energy carrier | kWh
Electricity import | ETS chiller | electricity | 1152112.0481
Electricity import | Central chiller | electricity | 839295.4622
Dry cooler | Central chiller | plant heat rejection | 3998050.148
Dry cooler | Central chiller | plant cooling rejection | 478334.7776
Dry cooler | Economizer | plant heat rejection | 1.2289e-16
Dry cooler | Economizer | plant cooling rejection | 5.5569e-15
Central chiller | Reservoir loop | plant cooling | 3252513.2116
Central chiller | Reservoir loop | plant heating | 572092.9738
Reservoir loop | ETS chiller | ETS heat rejection | 5042133.6871
Reservoir loop | ETS chiller | ETS cooling rejection | 1066815.905
ETS chiller | Cooling load | cooling load | 5381027.9018
ETS chiller | Heating load | space heating load | 1446576.5097
ETS chiller | DHW load | domestic hot water | 1144965.1054
Reservoir loop | Ground | ground anergy | 404988.3068
Ground | Reservoir loop | ground anergy | 96137.2486
Economizer | Reservoir loop | plant heating | 5.5569e-15
Economizer | Reservoir loop | plant cooling | 1.2289e-16
Borefield center | Reservoir loop | borefield center anergy | 2594636.4485
Reservoir loop | Borefield center | borefield center anergy | 3086467.2762
Borefield perimeter | Reservoir loop | borefield perimeter anergy | 180840.0742
Reservoir loop | Borefield perimeter | borefield perimeter anergy | 550768.9192

## Summer
From | To | Energy carrier | kWh
Electricity import | ETS chiller | electricity | 1310586.0026
Electricity import | Central chiller | electricity | 1472672.5942
Dry cooler | Central chiller | plant heat rejection | 6386511.1531
Dry cooler | Central chiller | plant cooling rejection | 0
Dry cooler | Economizer | plant heat rejection | 1033.4622
Dry cooler | Economizer | plant cooling rejection | 83896.9979
Central chiller | Reservoir loop | plant cooling | 4913937.865
Central chiller | Reservoir loop | plant heating | 0
Reservoir loop | ETS chiller | ETS heat rejection | 7639844.0948
Reservoir loop | ETS chiller | ETS cooling rejection | 15067.7739
ETS chiller | Cooling load | cooling load | 7435267.0264
ETS chiller | Heating load | space heating load | 462429.5658
ETS chiller | DHW load | domestic hot water | 666783.3395
Reservoir loop | Ground | ground anergy | 98150.6678
Ground | Reservoir loop | ground anergy | 95931.991
Economizer | Reservoir loop | plant heating | 83896.9979
Economizer | Reservoir loop | plant cooling | 1033.4622
Borefield center | Reservoir loop | borefield center anergy | 125543.4027
Reservoir loop | Borefield center | borefield center anergy | 2270767.7853
Borefield perimeter | Reservoir loop | borefield perimeter anergy | 11809.9704
Reservoir loop | Borefield perimeter | borefield perimeter anergy | 490381.1507

## Fall
From | To | Energy carrier | kWh
Electricity import | ETS chiller | electricity | 568599.0609
Electricity import | Central chiller | electricity | 382765.7546
Dry cooler | Central chiller | plant heat rejection | 1515576.3211
Dry cooler | Central chiller | plant cooling rejection | 613336.9908
Dry cooler | Economizer | plant heat rejection | 3.3196e-15
Dry cooler | Economizer | plant cooling rejection | 1.3414e-16
Central chiller | Reservoir loop | plant cooling | 1305747.9706
Central chiller | Reservoir loop | plant heating | 786263.3094
Reservoir loop | ETS chiller | ETS heat rejection | 2269718.5682
Reservoir loop | ETS chiller | ETS cooling rejection | 743458.8618
ETS chiller | Cooling load | cooling load | 2466080.2735
ETS chiller | Heating load | space heating load | 981410.8126
ETS chiller | DHW load | domestic hot water | 536938.7923
Reservoir loop | Ground | ground anergy | 114820.0605
Ground | Reservoir loop | ground anergy | 102650.106
Economizer | Reservoir loop | plant heating | 1.3414e-16
Economizer | Reservoir loop | plant cooling | 3.3196e-15
Borefield center | Reservoir loop | borefield center anergy | 192906.0304
Reservoir loop | Borefield center | borefield center anergy | 1148359.684
Borefield perimeter | Reservoir loop | borefield perimeter anergy | 158612.9035
Reservoir loop | Borefield perimeter | borefield perimeter anergy | 197339.5786